## Checklist (hidden)
This is a list of steps to fully lock and launch an updated tool
Step | Description
1 | Save the most recent unlocked tool as a new copy of the tool with "Vx.n+1 unlocked"
2 | Update tool as needed
3 | If adding new rows/data to the inputs tab make sure the cells have the correct protection (Font > Protection > check or uncheck "Locked")
4 | Fill out the Version Summary table on the Tool information tab. Make note of changes, especially when updates will change the incentive or savings. If this is a new version for a new year, remove the summary from the prior tool and only include major differences from prior year in V1.0
5 | Save a new copy of the file withouth "unlocked" in the file name
6 | If this is a new version of the tool for a new year create a new word doc in the tool folder with the updated password
7 | Protect tabs - all tabs, visible or not, should have a password protection. Use the same password as documented in the word doc
8 | Hide Tabs as follows. Very hidden tabs can be hidden by right clicking any tab > View Code > find each sheet in the Project window > Select "2 - xlSheetVeryHidden" from the final selection. Tabs for Very Hidden: - All sequence of operation tabs - Building Savings - Project Savings - Equipment and SOO - Incentive Calcs - Assumptions - for analysis in rows - Checklist - Tables
9 | Protect worksheet - go to File > Info > Protect Workbook > Protect Workbook Structure. Use the same password as saved in the word document
10 | Save the most recent unlocked tool as a new copy of the tool with "Vx.n+1 unlocked"
11 | Do a final check to ensure inputs can be edited, all data on the inputs tab is either cleared or default, and the following tabs are visible: - Tool Information - Program Information - Sequence Eligibility - User Inputs and Savings - PA Only - Pre-Inspectino - PA Only - MRD - Project Notes - EUI table
12 | Send the File to Lisa Zagura at Eversource to update to the Mass Save website

## Tool Overview (hidden)
Overview of 2024 BMS Calculator Savings Calculations
Last updated for BMS Tool Version 2024 V1.0
Updated 4/22/2024
Whitney Brougher, National Grid
Contents
Savings Overview
Foundational Analysis and Approach
Limitations and Additional Adjustments for Eligible Equipment
Project Estimates
Static tabs
Assumption tab
Building Savings Tab
Theoretical Savings tabs
Equipment and SOO tab
Equipment and SOO Eligibility table
Theoretical savings table
Percent Cooling vs. Ventilation Tables
Savings Potential Table
Project Savings Calculation
Conversions
Project Selections and References
EUI and Savings Potential - Project Area and Building
SOO % Allocation Values
Project Savings – kBtu
Savings Overview |  | Tab Reference
The BMS tool is intended to produce reasonable, average buildings savings without requiring detailed project level information. It is important that a realistic baseline is considered, but rather than capturing that baseline on specific projects, we are capturing it across the population. The program theory is that most buildings have some control, but not optimized control, so if all of our participants leave the program with optimized control we have produced savings. Under this framework we do not need to prove incremental savings on every building, but rather establish a “some control” baseline across the population and “optimized outcome” on each building.
To support this effort the BMS tool was developed to provide reasonable typical savings without onerous time or effort needed to document project baselines. Past program savings approaches have struggled to account for realistic total savings (top down, % building consumption savings) and sequence level savings estimates (bottoms up, sequence specific savings). Top down analysis anchors savings in reality, but does not provide enough granularity to account for different types of sequences implemented at different sites. On the other hand, bottoms up analysis may be reasonable for each sequence, but often sums up to unrealistically high totals.
Foundational Analysis and Approach
There are two main pieces of analysis used as the foundation of our savings approach:
· Building % Savings Potential – a billing analysis was performed to establish average bill savings, gas and electric, across past participants who did “significant” control work on their building. Each of these participants had some level of control before the project, meaning that the analysis should capture existing conditions and the final controlled state of the building. We use this as an assumed maximum saving potential in the tool.
o Note that we have not accounted for HVAC equipment or sequences implemented on these projects.
· Theoretical Savings for each SOO – an engineering analysis was performed for each sequence to establish maximum theoretical savings (kBtu/sqft) for each sequence using “typical” building characteristics. The savings were established using, as far as possible, common assumptions so there should be internal consistency across the estimates. We therefore assume that these savings, while not appropriate to apply directly to a particular building, do represent realistic relative savings for different sequences.
o Savings are considered for cooling equipment (chiller or DX), heating equipment (assumed a non-condensing boiler), and ventilation fans (CV or VAV)
o Savings assume 5 day operation with unoccupied nights
The tool considers the Building % Savings Potential to be the maximum savings for any building implementing all possible sequences. The Savings Potential is allocated across the sequences using the Theoretical Savings as a weighting factor. This results in a sequence specific % building consumption savings estimate, where if all sequences are implemented the sum of the savings will be the Building % Savings Potential. This allows us to take advantage of the realism of top down savings estimates and the specificity of bottoms up.
The electric building savings potential represents cooling and pump and fan savings, but we’ve developed independent theoretical savings estimates for chillers, DX cooling, VAV air handlers, and CV air handlers. In order to allocate out the savings potential we have to combine cooling and pump/fan savings, which means we have to make 4 combinations of equipment:
· DX cooling + CV air handlers
· DX cooling + VAV air handlers
· Chillers + CV air handlers
· Chillers + VAV air handlers
Limitations and Additional Adjustments for Eligible Equipment
Electric Sequence Savings
Because we have a single building % savings potential value, our approach is forcing all four of those scenarios to sum up to the same total savings potential, even though we would expect the savings to be different in the real world. This also means that the tool will return different savings potential for a given sequence depending on what equipment is used, even if the equipment has no impact on the savings in the real world. For example, Optimal start/stop has a theoretical fan savings of 0.04 kWh/sqft for both CV and VAV systems. However, the sequence savings potential in the tool is 0.4% for buildings with DX cooling and CV air handlers, but 1% for buildings with Dx cooling and VAV air handlers.
The difference is so large not because we would expect vastly different savings across these buildings, but because CV systems have a much higher theoretical savings for scheduling and setbacks, which means that other sequences are allocated a smaller share of the building potential. We have decided not to address this within the tool, accepting it as one of the trade offs of our simplified approach. We did not have enough data to produce or justify more granularity in the Building % savings potential, which could potentially correct for this effect.
Savings Potential When No cooling or Ventilation Selected
As discussed in the previous section, there is a complication in the tool where the % building savings potential represents both fan savings and cooling savings and no matter what combination of equipment is selected the tool will force the savings to sum up to the Building % Savings potential. However, when the project doesn’t have mechanical ventilation selected, we do not want to force the cooling savings only to sum up to the Building % Savings total, and vise versa when there is no cooling selected.
As a work around, we looked at the average % savings attributed to ventilation across the 4 potential combinations of cooling and ventilation equipment, which is about 63%. We then apply that value to the building % savings potential to isolate the ventilation only savings potential.
Building Occupancy
One of the major drivers of savings will be how the building is occupied- a building that is occupied 24/7 will not be able to do setbacks, for example, which is the biggest source of control savings. Rather than asking for existing control schedules, we only ask users for how the building is generally occupied – 24/7, 7 days with unoccupied nights, or 5-6 days with unoccupied nights. The theoretical savings were only developed for 5 day operations.
Our savings potential is adjusted using simple ratios to scale down scheduling and OSS potential for 7 day operation, remove those savings for 24/7 operation. All other sequences are scaled up for 7 day or 24/7 day operation since those savings occur during occupied hours.
Chiller Savings Potential
Because chillers have additional energy SOO compared to DX systems we believe there to be more savings potential for chiller systems. As stated above, we do not have actual kWh savings potential for chiller systems compared to DX systems. We decided to provide chiller systems an additional 1% building savings potential to account for the difference.
Heating System Efficiencies
The theoretical savings were developed for non-condensing boilers, but our program supports a range of heating systems. To apply the theoretical savings to other equipment types, we sourced average heating system efficiencies from evaluation reports and adjusted the savings potential using the relative efficiencies of non-condensing boilers and other heating systems (including electric heating systems).
This has the overall effect of also adjusting the building savings potential based on equipment type. A steam boiler, our least efficient heating system, will have greater building savings potential than other heating systems.
Electric Heat Building Savings Potential
The Building % Savings potential did not include any electric heat projects. We have assumed that the heating savings potential will also apply to electric heat savings potential. This concession was taken for simplicity and due to lack of other available research or assumptions.
To apply the heating savings potential we looked to CBECs data to identify an assumption of % building electric consumption used for electric heating for either resistance heat or heat pumps.
Non-Applicable Sequences and Savings Potential
Some equipment cannot support certain sequences, for example a furnace cannot implement hot water reset. In these cases we first adjust for heating system efficiencies and then remove non-applicable sequences. This means that some equipment will have lower building savings potential because they cannot implement all sequences.
Project Estimates
At this point in the analysis we have established a basis of determining the % building savings for each sequence given a certain set of equipment. The final component of the analysis is to scale that savings potential to the project.
EUI analysis
We collect annual fuel consumption and electric consumption as well as total building area as part of the tool. This is used to calculate electric EUI, fuel EUI, and total building EUIs.
Using the electric heat building savings potential assumptions mentioned above we can establish an electric heat EUI as well.
The tool assumes the same energy intensity across the building, but will account for electric heat in specific areas. This is a concession for simplicity and low volume of electric heat expected in our projects.
Area Savings Potential
The tool looks at each specified project area independently, meaning that the steps and adjustments listed above are applied to each area. This results in each area having a particular % savings potential.
Scaling Savings
The final step of the savings estimate is to multiply through the area EUI, the specified building area from the project inputs, and the % sequence savings for selected project sequences.
Static tabs
Overview of tabs that are static and do not change based on project inputs.
Assumption tab
Long list of assumptions that feed into some of the following tabs. Included citations or explanations when we have them, but if they’re blank they are “engineering assumptions”.
Building Savings Tab
We establish a building savings potential based on a billing analysis of past projects. The idea here is that a billing analysis will capture existing building control across a population, which means that we don’t have to capture that nuance on specific projects. The analysis could be more robust (more and more varied sites), but the result seems conservative and in line with other research.
Note that the gas analysis was weather normalized, but the electric analysis was not.
Theoretical Savings tabs
These are mostly hidden on the workbook, there’s one for each sequence. We establish “theoretical” savings for each sequence using typical building and operating characteristics on a per sqft basis. The theoretical savings differentiate between DX or chillers for cooling, VAV or CV for air handlers, and non-condensing boilers.
With the exception of Scheduling and Unoccupied Setbacks, the theoretical savings all represent a maximum savings potential, going from no control to control. We decided to include some unoccupied hours in the scheduling sequence since we believe that will be the case in most buildings and to provide more savings potential to other sequences.
Equipment and SOO tab
This tab summarizes or consolidates information from other tabs into a number of tables that are directly referenced for project calculations.
Equipment and SOO Eligibility table
This is one of my main reference tables that helps map project selections to the savings
· Full equipment list with unique references
· Savings references – because we don’t have theoretical savings for each piece of equipment, we need to map the equipment to the theoretical savings and make adjustments based on system efficiency. That’s what’s happening in these columns-
o the heating system adjustments directly adjust the non-condensing boiler theoretical savings to the heating equipment based on assumed efficiencies
o ventilation savings are mapped to either the theoretical savings associated with VAV or CV air handlers
· Sequence eligibility – there are some additional bits of logic elsewhere, but basically a 1 indicates that sequence will return savings for the particular equipment listed
Theoretical savings table
Theoretical savings are ported over from all of the theoretical tabs.
Also in this table are the adjustments we use to account for differences in the building occupancy- some sequences will save more if the building is occupied more, some will save less. Notable, if the building is occupied 24/7 we zero out the scheduling and optimal start/stop savings.
Percent Cooling vs. Ventilation Tables
Calculation of average saving attributed to cooling or ventilation. This is used to isolate cooling vs. ventilation savings potential for projects that do not have both.
Savings Potential Table
Additional adjustments possible to the buildings savings potential based on equipment selection:
1. We added an additional 1% electric savings potential if a chiller is used. This wasn’t scientific, but more sequences can be implemented and we expect higher savings possible
2. We apply the adjustments from the prior table to establish savings potential for ventilation only or for cooling only
3. Note that there’s a table starting in row 77 that includes % savings potential based on project type- that’s still in there in case we use it later, but they’re all the same value for now
Project Savings Calculation
This is where the static information above is applied based on provided user inputs. Pretty much all calculations are repeated across the project areas and then summed as a total. The calculations must be repeated because the equipment selection establishes the savings potential and sequence eligibility, which may be different in different areas of the building.
Conversions
This table flags what fuel is used on the project and provides energy conversion factors. The sections outlined here match sections on this tab in the tool. Additional information and assumptions are also given in the tool.
Project Selections and References
This table directly pulls in selections from the input tab and then looks up the references used in the calculations. The Inputs and References should be pretty straightforward
· Inputs - Area used – based on whether area sqft is provided
· Inputs - Project type – will pull from the proposed control activity or from the Project Information section if “Mix of Project Types” is selected
General Sequence Eligibility – this is where we start establishing some additional eligibility considerations outside of just the equipment. The section with 1/0 by sequences is used for conditional formatting on the input tab
EUI and Savings Potential - Project Area and Building
This includes the EUI analysis for each section. Assumes equal energy intensity throughout the building and allocates out consumption based on controlled sqft.
For electric heat – the assumption of % electric consumption used for heating is applied to each area. There is no adjustment to either electric or fuel consumption in other areas based on electric heat in one area, even though it falls to reason that gas not consumed in one area of the building would be concentrated elsewhere.
This also pulls in the appropriate % savings potential from the Equipment and SOO tab. Note that we are taking those building % savings values and applying them to each area of the building independently. This means that one area of the building with a chiller may have ~13% savings potential for consumption in that area, but another section of the building with no cooling will have 7.7% savings potential of the consumption in that area.
SOO % Allocation Values
This section establishes the portion of the % building savings that will be attributed to each sequence in an area of the building based on the equipment selected.
These values are dynamic in this tool only because the equipment is so variable and I didn’t want to create a big static table that included all the various equipment combinations. This doesn’t take any project specific information into account besides to pick the correct theoretical savings references.
The values are separated out based on the available % building savings potential categories:
· Cooling and ventilation
· Electric heating
· Fuel
Project Savings – kBtu
This table does the math of multiplying the information established earlier in the workbook for each sequence and each project area
· Building % savings potential
· Area EUI
· Area sqft
· % allocation
· Adjustment for building occupancy
· Ventilation adjustment (zero out certain savings if there is no mechanical ventilation)
· User selection of the sequence on the input tab
Subscription based controls that qualify for the optimization sequences have a final step of adding an additional 3% savings on top of the savings estimated above.

## Tool Information
Prescriptive BMS Calculator
Purpose
This tool was developed for the implementation of the Prescriptive BMS program. Actual customer energy savings will vary depending on existing control strategies, HVAC equipment condition, etc. This tool is intended to estimate incentives as well as average savings for projects with similar equipment, operating schedules, and implemented sequences, not site specific savings estimates. This tool should NOT be used for any project reported through a custom pathway.
Instructions and Explanations
Users must provide required information as described below.
| Tab |  | Section | Purpose and instruction
| Program Information |  | Terminology table | Definitions and explanation of program terminology, incentives, and eligibility.
| Sequence Eligibility |  | Table | Full detail for sequence eligibility by equipment type
| User Inputs and Savings |  | Building Energy Use Intensity | Provide basic information about the building used to estimate building Energy Use Intensity (EUI). Building energy consumption is required for savings results. Benchmark EUI values are provided as a check on provided building area and consumption.
|  |  | Control System Information | Provide information about the proposed control system installation. Includes proposed system type, installation costs, and interest in Active Demand Response.
|  |  | Affected Areas | Tool allows for 5 distinct areas of the building. The building areas must not overlap. Also collects information on the project area occupancy schedule, size, and project type.
|  |  | Controlled HVAC Equipment | Equipment serving project area.
|  |  | Sequences of Operation | Enter "1" when sequence is intended to be implemented in the area. Greyed out sequences will not provide incentives or savings based on provided HVAC system information
|  |  | Additional Optimization (Subscription Based System Control Only) | Area to request consideration for additional optimization and energy saving sequences provided by subscription based products. Consideration for additional sequences are subject to Massachusetts Technology Assessment Committee (MTAC) review.
|  |  | Results - Energy Savings | Electric energy, electric demand, and fossil fuel savings based on provided project and site information. Savings are provided separately for each project type.
|  |  | Results - Incentives | Summary of incentives by total, project type, and fuel type.
|  |  | Results - Other Results | Summary of project impacts on building, including area controlled, percent building energy savings, and estimated consumption for controlled building area.
|  |  | Feedback on Missing Results | Table summary of any data entry issues that are resulting in missing or hidden project results.
| PA Only - Pre-Inspection Checklist |  | Form | PA Tab - Shared PA resource for documenting project pre-inspections. May be printed.
| PA Only - MRD Equipment List |  | Equipment Description and Tags | Enter groups of similar equipment that are controlled with the same sequences. This is used to populate the project MRD. Unique equipment or equipment with different sequences applied should have their own line item.
|  |  | Sequences of Operation | Enter "1" when sequence is enabled on listed equipment. Greyed out sequences will not provide incentives or savings based on provided HVAC system information
| PA Only - Project MRD |  | Minimum Requirements Document (MRD) | Autofilled based on MRD Equipment List and User Inputs and Savings information. The MRD lists required trend data and documentation for project close out based on the sequence(s) implemented.
| EUI Benchmark |  | Project EUI Feedback | Comparison of project EUI values to benchmark EUI values. The comparison is for QC purposes only. Projects outside of expected range can review entered data for accuracy.
|  |  | Benchmark EUI | Table developed from CBECS and National Grid customer information. For informational purposes only to provide check against tool calculated EUI data.
| Project Notes - Optional |  | Project Notes | Space for project notes and explanations.
Version Information
| Version Name | 2025 Prescriptive BMS Calculator
| Version Number | 2026 V1.0
| Version Date | 2026-01-15
| Last Revised by | Whitney Brougher, National Grid; Lisa Zagura, Eversource; Zack Lippert, National Grid
Revision History
| 2025-01-01 |  | 1 | Significant tool updates from 2024 Prescriptive BMS Calculator: - Remove lower building area limit - Allow incentives for controls implemented on new equipment, with exceptions for change in space use, building additions, and participants in the New Construction & Major Renovations pathways. - Update to Summer kW calculation to align with other tools. Remove Economizer Control energy savings from consideration given the very small overlap with peak periods. Update approach multiplies kWh savings by a conversion factor and multiplies with coincidence factors.
| 2025-04-23 |  | 1.1 | - Added field to indicate whether controlled equipment is new - Corrected conversion to gallons of oil and propane. - Corrected error that blocked results from displaying when cooling and ventillation are excluded from project - Corrected logic for HP heating scheduling eligibility
| 2026-01-15 |  | 1 | - Updated tool hyperlinks -Adjusted ADR kicker to $3k or $500 based on 1.5million kWh annual usage

## Program Information
Prescriptive BMS Calculator Version
Tool Version | 2026 V1.0
Glossary Revision Date | 2026-01-15
Category | Topic | Description | Example/Explanation | Last Updated
Eligibility | Eligible and Ineligible Buildings and Systems | Eligible buildings must meet the following: - Commercial buildings and meters - Total building area under 300,000 sqft - Comfort space conditioning loads - Electric, oil, propane, and/or gas used for space conditioning The following are not eligible under the Prescriptive BMS program: - Buildings with significant process or lab loads. Custom incentives may be available. - Stand alone front-end upgrades or software updates - Building spaces with new loads or significant changes to how a space is used - Buildings participating in the Mass Save New Construction & Major Renovations program - Replacements of existing BMS that are less than 15 years old - Sequences of operation and BMS that have already received a rebate or incentive from a Sponsor of Mass Save within the last 5 years, excluding subscription products. | Projects that do not meet this criteria may be eligible for custom incentives. Examples of eligible projects: - New controls installed along with HVAC equipment replacements, as long as the new equipment serves existing conditioned spaces and loads. | 2025-01-01
Eligibility | Eligible and Ineligible Control Systems and Products | The Prescriptive BMS program includes control systems with energy saving sequences maintained remotely or maintained on site. Building control systems are required to monitor and control all building parameters (read-write) associated with the sequences of operation from the singular central location. To be eligible, any proposed control system must meet all of the following criteria: - Control eligible HVAC equipment - Implement or optimize at least one eligible energy efficiency sequence and provide information outlining the parameters and components involved (including but not limited to damper signals, temperature set points, pressure set points, etc.) - Must show and be able to adjust building parameters associated with energy sequences comprehensively in one location - Must be able to meet trend data requirements as outlined in the Minimum Requirements Document (MRD) - Implement or optimize sequences of operation (SOO) on existing building equipment Systems may include other features, such as FDD, dashboards to view computed data, continuous optimization, machine learning, etc., but must meet the above minimum criteria to be eligible. | Examples of eligible projects: - Installation of control panels and components to implement eligible sequences of operation on existing equipment that can be viewed and controlled from a central location - Installation of system based controls that allow for interoperability between systems and use AI to optimize system performance through a subscription based system that monitors and controls sequence performance from a central location Examples of ineligible projects: - Installation of controls on standalone equipment that is not capable of centralized/building level monitoring or control - Installation or replacement of a server, laptop, or firmware, etc. without optimizing or implementing eligible sequences of operation - Installation of thermostats that are centrally monitored and allow remote setpoint adjustment, but do not provide other energy savings sequences (these projects may be eligible for thermostat rebates) - Systems that do not centrally monitor and collect building trend data for export in Excel format to perform the project verification as required by the MRD | 2025-01-10
Eligibility | Project Type: Upgrade of Existing BMS | The Prescriptive BMS program will provide incentives for upgrades to existing BMS. Upgrades may include adding new energy savings sequences of operation or optimization of existing sequences of operation. | Example 1: First time addition of DCV in school gymnasium on an existing air handler Example 2: Bringing two existing RTUs currently operating with standalone control under an existing central BMS and the customer will be adding DCV control. If existing stand along control includes schedule and OSS, customer receives BMS incentives for schedule and setbacks, OSS, and DCV control. Example 3: Changing the constant discharge pressure setpoint of the lobby air handlers to one that modulates dependent on system demand. Example 4: Revisit and optimize existing energy sequences as part of a firmware update project. | 2024-03-11
Eligibility | Project Type: Installation of New BMS | The Prescriptive BMS program will provide incentives for installations of new traditional building management and control systems. Projects may include first time installations or replacements of legacy systems. To qualify for System Replacement incentives: - Front end software, building supervisory software, or field panel hardware are demonstrated (via pre-inspection) to be older than 15 years. - The installation of the building control must be on existing building equipment. Incentives for energy savings can be attributed to the installation of control for new building equipment. | Example 1: Building currently using thermostats for standalone air handler scheduling and setback and standalone third party device for hot water reset on boilers. Customer would like to install a new centralized BMS. The customer would like to receive incentives for schedule and setbacks, optimal start-stop (OSS), and hot water reset when BMS is installed on existing equipment. Example 2: Customer shares their pneumatic system with controllers 15 years old no longer can carry out hot water reset nor basic scheduling on some of the major HVAC equipment. After reviewing of drawings and field panel dates of manufacture, the system is determined to be 20 years old. Customer is eligible for incentives. Example of INELIGIBLE project: Customer has an 8 year old system that is operating poorly. Schedules have been over written. Customer is not eligible for Installation of New BMS incentives but should consider Upgrade of Existing BMS incentives to improve their existing system. | 2024-02-29
Eligibility | Project Type: Subscription Based System Control | The Prescriptive BMS program will provide incentives for installation of subscription system based control. These system control products must meet the criteria listed under "Eligible Control Systems and Products". Subscription systems require annual fees to access the full suite of energy saving sequences of operation. Subscription based control products may include hardware installations that will maintain basic control on site even when "offline". Product must be reviewed by the Massachusetts Technology Assessment Committee (MTAC) team prior to recieving project incentives. | The following will not qualify for subscription based system control incentives on their own: - Control of standalone of equipment - Age of workstation operating system software (Windows, etc.) - Age of communication/translation cards to enable new sequences at existing standalone devices to achieve eligible sequences of operation which otherwise had not been implemented - Issues or Age of software drivers that interface between factory controllers and an existing front-end software to achieve eligible energy savings sequences - Technology or control products that have not been reviewed by MTAC - Though building control products may include subscription fees for access to additional features that do not directly control equipment, such as fault detection and diagnostics (FDD), dashboard access, service contract fees or updates, etc., these will not be considered subscription-based system control projects. | 2024-03-11
Eligibility | HVAC Equipment | The Prescriptive BMS program provides incentives for the following major equipment: - Boilers - Furnaces - Gas fired heat in AHU - Electric Resistance in AHU - Electric Baseboards - Air Source Heat Pumps - Variable Refrigerant Flow (VRF) systems - Water Loop Heat Pumps - Chillers - Central DX cooling - Control of terminal units without control of major equipment The following are NOT eligible under the Prescriptive BMS program: - Controlling process or lab loads - Control of new equipment serving significant new loads or newly conditioned spaces | Project equipment not included in the prescriptive BMS program may be eligible for custom incentives. | 2024-03-11
Eligibility | Sequences of Operation | The Prescriptive BMS program provides incentives for the following Sequences: - System Schedule and Unoccupied Setbacks - Optimal Start/Stop - Reset Supply Air Pressure - Reset Boiler Water Temperature - Demand Control Ventilation - Economizer Control (Dry Bulb or Dual Enthalpy) - Reset Supply Air Discharge Temperature - Reset Chilled Water Temperature - Reset Condenser Water Temperature | Sequence eligibility for a particular project will depend on building occupancy and major HVAC equipment controlled. See Mass Save prescriptive BMS application form for more detail. Projects including sequences outside of this list may apply for custom project incentives. | 2024-03-11
Eligibility | Additional Optimization Sequences (Subscription based controls only) | Acknowledging that some subscription based products may implement a narrow set of eligible sequences, but may offer additional energy saving features and sequences outside of the current list, the Sponsors of Mass Save are making a general category available for cooling, ventilation, and heating optimization beyond the eligible sequences listed. Use of these additional categories is subject to review by MTAC. Please work with MTAC to provide an explanation of how the optimization features work and to save energy. If approved, each eligible and additional general category sequence will be eligible for incentive. | Example of eligible use: A product provides scheduling and optimal start/stop for RTUs, making them eligible for 4 incentive sequences (see Counting Eligible Sequences explanation below). In addition, the software will optimize RTU staging, reduce ventilation fan use, and reduce overheating. After MTAC review, the project is approved for an additional 2 sequences. The product provides centralized monitoring and control of the associated system points and allows for centralized trend data collection. Example of ineligible use: A product provides scheduling and optimal start/stop for RTUs, but does not provide the necessary system trend information nor provides a central location to view and adjust sequence parameters. In addition, the product was not reviewed by MTAC. | 2024-03-11
Eligibility | Building Control and Active Demand Response (ADR) Enrollment | The Sponsors of Mass Save will provide an additional incentive for building control systems that include temporary curtailment sequences as part of their project and enroll in the ConnectedSolutions program for the first time. To be eligible for this additional incentive: - Project meets all Prescriptive BMS program criteria - Building control system project must include the implementation or optimization of at least two eligible electric energy savings sequences of operation - Facility has not previously enrolled in ConnectedSolutions - Final project documentation includes proof of ConnectedSolutions enrollment from the Curtailment Service Provider (CSP) | The Curtailment Service Provider (CSP) will help make your building Active Demand Response (ADR) ready by identifying what equipment can respond to a Demand Response event and testing the system after installment so you are ready for enrollment and participation. The following list are Curtailment Service Providers serving Massachusetts: CPOWER: Call 1-844-276-9371 Enel-X: Call 1-617-692-2514 IPKeys: Call 1-855-475-3970 Voltus: Call 415-463-4236 | 2026-01-15
Incentives | Project Type: Upgrade of Existing BMS | Incentive Rate: $0.05 / sequence count / sqft | Add On or Optimization of Existing BMS | 2024-03-11
Incentives | Project Type: Installation of New BMS | Incentive Rate: $0.10 / sequence count / sqft | Installation or Replacement of New BMS | 2024-03-11
Incentives | Project Type: Subscription Based System Control | Incentive Rate First Year Scheduling: $0.10 / sqft Incentive Rate: $0.01 / sequence count / sqft / prepaid year | First Year Scheduling rate available when project includes hardware installation that will provide customer basic "offline" control of equipment. | 2024-03-11
Incentives | Counting Eligible Sequences for Incentives | The sequence count will consider what fuel savings result from implemented sequences. Sequences that produce both gas and electric savings will provide two sequence counts, whereas a sequence resulting in a single fuel savings will provide one sequence count. Four eligible sequences may produce gas and electric savings, depending on selected equipment: Scheduling and Unoccupied Setbacks, Optimal Start/Stop, Demand Control Ventilation, and Supply Air Discharge Temperature Reset. The maximum sequence count is 13. Subscription Based System Control may also be eligible for one or more of the Additional Optimization sequences. |  | 2024-03-11
Incentives | Calculating Incentives - Standard BMS Project Types | Incentives are calculated for each building Affected Area as provided on the User Inputs and Savings tab. Incentives are calculated discretely based on the affected area entered, eligible sequence count, and the Project Type's incentive tier. | (Area Incentives) = (Affected Area) * (Sequence Count) * (Incentive Rate Based on Project Type) | 2024-03-11
Incentives | Calculating Incentives - Subscription Based Control System | Incentives are calculated for each building Affected Area as provided on the User Inputs and Savings tab. Incentives are calculated discretely based on the affected area entered, eligible sequence count, and number of prepaid years of subscription. First year installations with a hardware component will be eligible for increased incentives. | First year: Area Incentives = (Affected Area) * (Scheduling @ $0.10 / sqft) + (Affected Area) * (Sequence Count @ $0.01 / sqft / SOO) * (# Pre-paid years of subscription) Subscription Renewals: Area Incentives = (Affected Area) * (Sequence Count @ $0.01 / sqft / SOO) * (# Pre-paid years of subscription) | 2024-03-11
Incentives | Project Incentive Cap | Energy efficiency project incentives are capped at 60% of the total project costs. The Active Demand Response enrollment incentive is not included in the project cap. | Example: A new BMS installation is invoiced at $100,000 and includes the implementation of 5 SOO over a 150,000 sqft project area. - Incentive cap = ($100,000) x (60%) = $60,000 - Calculated project incentive = (150,000 sqft) x (5 SOO) x ($0.10 / SOO / sqft) = $75,000 - The calculated project incentive exceeds the incentive cap - Eligible incentive = project incentive cap = $60,000 If the project includes Active Demand Response enrollment, then - Eligible incentive = $63,000 | 2024-03-11
Incentives | Incentive Allocations | Total project incentives are allocated between gas and electric Sponsors of Mass Save relative to applicable energy savings. Customer must apply to both Sponsors to be eligible for the full incentive. The incentives are allocated based on expected project benefits, similar to the Mass Save Custom Screening Tool. | It is extremely important that both your gas AND electric Sponsors of Mass Save receive the application, calculator and other supporting documentation to be eligible for the gas and electric incentives if applicable. | 2024-03-11
Incentives | Building Control and Active Demand Response Enrollment Incentive | For eligible projects where customer: - implements at least two (2) electric energy savings SOO - implements temporary curtailment sequences - enrolls in the ConnectedSolutions active demand response program | Applied to first time building ADR enrollment as confirmed by CSP. Amount does not applied to 60% project incentive cap. | 2026-01-15
Terminology | Building Management System (BMS) or building control system | The Mass Save Prescriptive BMS program will provide incentives for qualified projects when the building control system includes the following: -Front end or building supervisory controller software which will support specified Sequence(s) of Operation (SOO) that will produce energy savings and allow for viewing and adjustment of project sequence parameters (setpoints, temperatures, pressures, CO2 concentrations, valve signals, damper signals, etc.). -BMS and building control projects will include installation or optimization of control panels or control points related to enacting eligible energy saving sequences of operation. -All BMS and building control projects will require trended data to verify the operation of sequences per the Minimum Requirements Document (MRD). -Though these building control products may include subscription fees for access to additional features that do not directly control equipment, such as fault detection and diagnostics (FDD), dashboard access, service contract fees or updates, etc. these will not be considered subscription based system control projects. | The building system control must control building systems. Equipment that is operating as standalone or being monitored independent of a central system are not for the purposes of this application controlling the building. The following control systems are not eligible for the Mass Save Prescriptive BMS program: -Front end or building supervisory controller software upgrades that do not add or optimize any new eligible control sequences of operation (SOO). -Front end or supervisory controllers that provide read only access to system points, not allowing for adjustments in sequence parameters. -Server, software, or firmware upgrades that do not include the addition or optimization of eligible control sequences of operation. -Thermostats with remote set point adjustment and/or control via remote application. These ineligible systems may have an outdoor air temperature algorithm in the control logic to operate heating and cooling systems | 2024-03-11
Terminology | Subscription Based System Control | Subscription Based System Control incentives support first time installations and annual subscription fees for the implementation of building system controls in existing buildings on existing equipment that meet program expectations for hardware and software as described in the BMS or building control Terminology above. To qualify for Subscription Based System Control incentives: There is no existing BMS serving the existing equipment that is less than 15 years old. Customer may have been using thermostats or standalone devices to control HVAC equipment prior to centralizing equipment to the subscription-based system controls. Subscription based system control products must be reviewed by the Massachusetts Technology Assessment Committee (MTAC) to be eligible for the prescriptive BMS incentive6 MTAC will determine the eligible sequences of operation the subscription-based control product is appropriate for and share with the manufacturer, customer, and technical review team. | The following scenarios will not qualify a project for subscription-based control product incentives on their own: -Control of standalone of equipment -Age of workstation operating system software (Windows, etc.) -Age of communication/translation cards to enable new sequences at existing standalone devices to achieve eligible sequences of operation which otherwise had not been implemented7 -Issues or age of software drivers that interface between factory controllers and an existing front-end software to achieve eligible energy savings sequences -Technology or control products that have not been reviewed by MTAC | 2024-03-11
Terminology | Building Supervisory Controller | Web-based control interfaces and cloud-based computing applications through which BMS are accessed and functionality is enabled. The traditional front end has been replaced with servers running supervisory and application software. The software has been designed to provide server-level functions for a network of other servers and other field devices. The hardware-software combination serves real-time information to standard web-browser clients and performs essential functions such as analytics, centralized data logging/trending, archiving to external databases, alarming. When a manufacturer moves from one type of hardware, there is typically a software upgrade needed, and the manufacturer decides what the backward compatibility of the new software will be. |  | 2023-03-20
Terminology | Front End | A front end consists of a BMS dedicated computer and monitor. This computer is where the BMS vendor will place the operating and programming software as well as other related application tools and trend archiving software. The important applications on the front end are programming; graphics development and display; global information and/or sharing; alarming; trend log archiving; and other typical computer applications. | The front end software described here are considered for Replacement incentive eligibility if demonstrated to be older than 15 years old. | 2024-03-11
Terminology | Field Panel | Field panels are available with various levels of functionality. Generally speaking they have direct input and output capabilities and usually have some level of supervisory role. Generally, the advantage of using a field panel is the ability to handle more input and output capacity, and to handle communication up and down the system network architecture. The field panels often have some level of memory and serve as a network buffer for communication traffic. | The field panel described here are considered for Replacement incentive eligibility when the majority of building field panels are demonstrated to be older than 15 years old. | 2024-03-11
Terminology | Terminal Device and Application Specific Controllers | These controllers are limited in the number of inputs and outputs, and in the case of application specific controllers, they may have a set of pre-programmed SOO’s for which only setpoints can be changed, not the programming. They also have limited communication and storage memory. One type of device is known as Original Equipment Manufacturer (OEM) packaged controls. These controllers are supplied by equipment manufacturers and are designed to be standalone controls. These controllers have application specific programming when shipped from the factory and usually can only have certain SOO’s enabled and/or adjusted as well as setpoint adjustments. These controllers usually can take a few inputs and supply a limited number of outputs. They usually can be provided with BACNET communication cards which have limited functionality enabled, however this is typically added at a cost. | The terminal device and application specific controllers are not included when considering Replacement incentive eligibility. | 2023-03-20
Terminology | System Schedule and Unoccupied Setbacks | Adjust scheduling on HVAC systems such as cooling tower fans, rooftop units, air handler fans, exhaust fans and electric resistance heating to align the operational hours with the occupancy of the space they serve. Implement temperature setbacks during unoccupied periods. | Sequence is not eligible for incentives in spaces occupied 24/7. | 2023-03-20
Terminology | Optimal Start/Stop | Programming the units to anticipate the heating or cooling needs of a space by starting equipment early enough to reach setpoint just at the beginning of scheduled occupancy, typically morning warm up/cool down. This is often done with air handling unit dampers closed. | Sequence is not eligible for incentives in spaces occupied 24/7 or on secondary heating systems. | 2023-03-20
Terminology | Reset Supply Air Pressure | Minimizes fan energy in VAV systems because the control system acknowledges when VAV box dampers are either partially closed or partially open and adjusts the static pressure based on this demand for conditioned air. |  | 2023-03-20
Terminology | Reset Boiler Water Temperature | Implement boiler reset controller to ensure automatic control of boiler water temperature based on outdoor air temperature, return water temperature, or demand for heating. Includes implementing HW OAT lockout. | Sequence is not eligible for incentives on secondary heating systems. | 2023-03-20
Terminology | Demand Control Ventilation | Maintain reduced amount of outdoor air circulating through air handling units unless a minimal threshold of CO2 is reached. The outdoor air increase will be proportional to the CO2 ppm in the space(s). In controlling a unit in this fashion, less of the outside air is then using energy to be conditioned. |  | 2023-03-20
Terminology | Economizer Control (Dry Bulb or Dual Enthalpy) | Using a comparison of the return and outdoor air dry bulb temps or enthalpy a determination of when cool outside air can be used to reduce the need for DX or chilled water cooling. |  | 2023-03-20
Terminology | Reset Supply Air Discharge Temperature | This measure reduces boiler energy in moderately cool weather by decreasing the discharge air temperature and increasing airflow to meet the room setpoint requirements; and reduces chiller energy in moderately warm weather by increasing discharge air temperature and increasing airflow to meet the room setpoint requirements. |  | 2023-03-20
Terminology | Reset Chilled Water Temperature | Implement the optimal operation of the controls adjusting the chilled water temperature to increase when outdoor air conditions allow and the building is experiencing a reduced demand for cooling. This type of sequence could involve a chilled water outside air temperature lockout. |  | 2024-03-11
Terminology | Reset Condenser Water Temperature | Condenser water reset is a control strategy that will optimize chiller performance. This strategy is only applicable to water-cooled chillers. The condenser water setpoint or the temperature of the water leaving the cooling tower can be controlled based on building loads, outdoor air wet-bulb temperature, or another appropriate control variable. |  | 2023-03-20
Terminology | Primary Building Activity (PBA) | Primary business, commerce, or function of the building. The PBA is used for EUI benchmarking and incentive allocation. | https://www.eia.gov/consumption/commercial/building-type-definitions.php#Service | 2023-03-20

## Sequence Eligibility
Eligible Equipment and Sequences of Operation
Purpose
This tab is a reference to understand what sequences are available for eligible sequences.
| Equipment |  | Eligible Sequences of Operation
| Equipment Category | Type | System Schedules and Unoccupied Setbacks [1] | Optimal Start / Stop [1] | Reset Chilled Water Temperature | Reset Static Pressure | Reset Boiler Water Temperature | Demand Control Ventilation [2] | Economizer Control - Dry Bulb or Dual Enthalpy | Reset Supply Air Discharge Temperature [2] | Reset Condenser Water Temperature
| Primary Central Heating System | Steam Boiler | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0
|  | Non-Condensing Boiler | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0
|  | Condensing Boiler | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0
|  | Furnace or Gas Heat in Air Handler [4] | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0
|  | Electric Resistance in Air Handler | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0
|  | Electric Resistance in Terminal Units | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Direct Expansion (ASHP, VRF, GSHP, AWHP) [3] | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
| Primary Central Cooling System | Direct Expansion (AC, ASHP, VRF, GSHP, AWHP) | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0
|  | Chiller | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1
| Primary Ventilation Type | CV Air Handler | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | VAV Air Handler | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0
|  | CV DOAS | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | VAV DOAS | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0
|  | Decentralized Ventilation (Unit ventilator, Fan Coil Units) | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Secondary Heating System to Heat Pump System | Steam Boiler | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0
|  | Non-Condensing Boiler | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0
|  | Condensing Boiler | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0
|  | Furnace or Gas Heat in Air Handler | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0
|  | Electric Resistance in Air Handler | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Electric Baseboard/Cabinet Heater | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Terminal Unit Type | Unit Ventilator | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Air Conditioning (PTAC or AC) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Packaged Terminal Heat Pump (PTHP) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Fan Powered Terminal Boxes (FPTB) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | CV Box | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | VAV Box | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Fan Coil Unit (FCU) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Baseboard, Cabinet Heater or Radiators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | VRF or ASHP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Water Loop Heat Pump | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Limitations and Exceptions
[1] Spaces with 24/7 occupancy are not eligible
[2] Only eligible when space has mechanical ventilation included in the project
[3] DX heating systems are not eligible for Scheduling and OSS with 7 day occupancy
[4] DCV not eligible for direct fire systems

## User Inputs and Savings
Jump to Results
| Statewide Savings Tool | Prescriptive BMS Calculator |  |  |  |  | Version N°: | 2026 V1.0 |  |  |  | Legend
| Company Name: | [5 empty] | Version Date: | 2026-01-15 |  |  |  | Application info
| Company Address: |  |  | Street |  | City | Gas PA: | Eversource Gas |  |  |  | User Input
| Customer Contact Name: |  |  | Phone N°: |  |  | Electric PA: | Eversource |  |  |  | Project Calculation
| PA Technical Representative: | [10 empty] | Not applicable to project
| PA Technical Representative Phone Number: |  |  |  |  | Application #:
Electric accounts associated with the building:
Gas accounts associated with the building:
This prescriptive BMS offer supports installation of new Building Mangament Systems, upgrades to existing systems, and implimentation of subscription based system control products.
[9 empty] | Flags for errors and conditional formating | Explanation
Instructions: Provide requested information for all orange cells. "*" Indicates required field for savings estimates or incentives. Click on [-] box on the left of the screen to collapse sections of the tool and [+] to expand.
Building Energy Use Intensity | [8 empty] | HIDE IN FINAL
| Select cell for description | User Input |  | Messages
Building Information
Select Principal building activity*
| Non-Electric Heating Fuel* | [7 empty] | #N/A | fuel type
| Total Building Area (sqft)* |  | Square Feet | Buildings must be under 300,000 sqft to be eligible for this program. Please seek custom savings incentives for larger buildings. |  |  |  |  | 0 | Flag if building too large for the program. Used for conditional formatting of cell E27
| Annual electric usage (total over last 12 months)* |  | kWh | Note that tab 1. Pre-Inspection indicates on site generation or industrial process loads at this site, which will affect the site EUI. |  |  |  |  | 0 | Flag if pre-inspection indicates renewables or process loads
| Annual fuel usage (total over last 12 months)* |  | - | [5 empty] | 1 | flag if area, kwh, or therms are blank
Site Energy Use Intensity - See EUI Benchmark tab for more detail
|  | Project | Benchmark | Units | Benchmark Comparisons
| Total Building EUI | Missing Data | #N/A | kBtu/sqft | The Total EUI isProvide requested project information for feedback.
| Electric EUI | Missing Data | #N/A | kBtu/sqft | The Electric EUI isProvide requested project information for feedback.
| Fuel EUI | Missing Data | #N/A | kBtu/sqft | The Fuel EUI isProvide requested project information for feedback.
Control System Information
| Select cell for description | User Input |  | Messages
Project Type
| Proposed Control activity* | [6 empty] | Click for additional BMS program information | #N/A | ref for control activity. Used for conditional formatting in project info section
| Will the proposed control activity include Demand Response Curtailment sequences? |  |  | Projects implementing at least 2 prescriptive electric energy efficiency sequences of operational and temporary demand curtailment sequences for the first time in their building may be eligible for an additional incentive. The Sponsors of Mass Save must receive confirmation enrollment with ConnectedSolutions from the Curtailment Service Provider (CSP) to receive the additional incentive. |  |  |  | Click for ConnectedSolutions Information | 1 | if "no" then this will be zero. Used to show message on ADR readiness requirements
Building Management System (BMS) or Building Control System The Mass Save Prescriptive BMS program will provide incentives for qualified projects when the building control system meets the Prescriptive BMS application criteria for centralized control and trending of existing equipment. The Sponsors of Mass Save will consider the project BMS as long as the energy saving sequences and system meet the application requirements.
| Proposed BMS Manufacturer and Product | [Product type] | [6 empty] | #N/A | flag if BMS. Used for incentive comparison to total cost
| Total Proposed Project Cost* | 100000 | [6 empty] | #N/A | flag if BMS, but cost not provided
| Notes/explanation on scope and cost | [Optional information about system capabilities, type, other information that may be relevant to project review and application processing]
Subscription Based System Control Subscription Based System Control incentives support first time installations and annual subscription fees for the implementation and maintenance of building system control sequences in existing buildings on existing equipment that meet program expectations for hardware and software. These control products must be reviewed by the Massachusetts Technology Assessment Committee (MTAC) prior to prescriptive program participation.
| Has this product been reviewed by MTAC and deemed eligible for this program? | Yes |  | #N/A |  |  | Current Reviewed Product List on BMS Website | Click for MTAC Product Submission Information | #N/A | flag if product not reviewed by MTAC and subscription project type = 1 | Products must be reviewed by MTAC prior to project approval.
| Proposed Control System Product | [Product type] |  | Provide product name and type. |  |  |  |  | #N/A | flag if subscription. Used for incentive comparison to total cost
| Is this the first year this product has been deployed at this site AND does the project require hardware upgrades at the site (such as compatible thermostats, new controllers, sensors, etc.)? * | 1 |  | First year implementation of subscription controls that include hardware installations will receive additional incentives to offset the cost of implementation. |  |  |  |  | #N/A | flag if subscription but cost not provided
Has this site received a BMS incentive for this subscription in a previous year? (1 = Yes)
| Number of years prepaid subscription on this application* | 5
| Proposed installation/integration costs (excluding subscription fee) included in this application* | 500000
| Proposed annual subscription fee ($/year)* | 1000 |  | Provide annual subscription cost, not total pre-paid value.
| Notes/explanation on scope and cost | [Optional information about system capabilities, type, other information that may be relevant to project review and application processing. Note, if available and applicable, past program participation]
Project Information
| Select cell for description | User Input |  |  |  |  | Messages
Affected Areas - Please provide an estimate square footage for each discrete building area impacted by the Sequences of Operation in the columns below. Project areas reas should not overlap. If all sequences affect same area, only populate "Area 1." One piece of equipment may serve multiple areas.
|  | Area 1 | Area 2 | Area 3 | Area 4 | Area 5 | Total Project Area
| Project Affected Area (sqft)* | [5 empty] | 0 | Affected area exceeds building area. Ensure Areas Do Not Overlap. | 0 | flag if total project area is larger than building area. Note, values must be whole numbers greater than (-1). Used for conditional formatting of cell E53
| Area Description |  | Retail | [description 3] | [description 4] | [description 5] | Project areas represent distinct spaces in the building and should not overlap. Project equipment may serve multiple Affected Areas.
| Area Occupancy* |  | 7 Day with Unoccupied Nights | 5-6 Day with Unoccupied Nights | 5-6 Day with Unoccupied Nights | 5-6 Day with Unoccupied Nights
| For "Mixed of BMS Project Type" proposed control activity - specify Control Activity In Affected Area | Installation of New BMS | Installation of New BMS | Installation of New BMS | Installation of New BMS | Installation of New BMS
| Controlled HVAC Equipment - Please provide information on the equipment that will be controlled in the affected area as part of this project. Please go in the order top to bottom, a this will effect the selections that come after. | [7 empty] | CONDITIONAL FORMATTING NOTES | default of all cells is like this | text
| Is any of the controlled HVAC equipment serving this space new or recently installed? | Unknown | No | Unknown | Unknown | Unknown | Select equipment serving each area. If equipment is not eligible (such as new equipment) mark "N/A or Not Controlled in Project". Terminal units not factored into savings or incentives.
| Ventilation System Type* | CV Air Handler | CV DOAS | N/A or Not Controlled in Project | N/A or Not Controlled in Project | N/A or Not Controlled in Project |  |  |  | when eligible, use this | text
| Primary Central Heating System* | Condensing Boiler | Direct Expansion (ASHP, VRF, GSHP, AWHP) | N/A or Not Controlled in Project | N/A or Not Controlled in Project | N/A or Not Controlled in Project
| Primary Central Cooling System* | Direct Expansion (AC, ASHP, VRF, GSHP, AWHP) | Direct Expansion (AC, ASHP, VRF, GSHP, AWHP) | N/A or Not Controlled in Project | N/A or Not Controlled in Project | N/A or Not Controlled in Project
| Majority Terminal Units | N/A or Not Controlled in Project | Fan Coil Unit (FCU) | N/A or Not Controlled in Project | N/A or Not Controlled in Project | N/A or Not Controlled in Project
| Secondary Heating System to Heat Pump System* | N/A or Not Controlled in Project | N/A or Not Controlled in Project | N/A or Not Controlled in Project | N/A or Not Controlled in Project | N/A or Not Controlled in Project |  |  |  | conditional formatting here based on bh_HP flag on project savings tab
| Sequences of Operation - Select "1" for each sequence to be implemented under each Affected Area. Selection of a proposed sequence for implementation should align with the submitted description of how each sequence intends to control (set points, control component operation, etc.). ++When "1" is bold the sequence contributes both heating and cooling/ventilation savings based on the selected equipment. | [7 empty] | unique use of eligible sequences |  | Sequence not Eligible if "0". Considers schedule and primary systems. Selection will grey if not eligible
| System Schedules and Unoccupied Setbacks++ | 1 | 0 | 0 | 0 | 0 | Select the sequences proposed for implementation in each area. Sequences that are grey are not eligible based on selected equipment and area occupancy. Ineligible sequences will not receive incentives or return savings. |  | #N/A |  | Valid except when 24/7 occupancy. No HP heating with 7 day schedule, but still savings on pumps and fans.
| Optimal Start / Stop++ | 1 | 0 | 0 | 0 | 0 |  |  | #N/A |  | Valid except when 24/7 occupancy. No HP heating with 7 day schedule, but still savings on pumps and fans.
| Reset Chilled Water Temperature | 1 | 0 | 0 | 0 | 0 |  |  | 0 |  | Valid when chiller used
| Reset Static Pressure | 1 | 0 | 0 | 0 | 0 |  |  | 0 |  | Valid when VAV selected
| Reset Boiler Water Temperature | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | Valid for condensing and non-condensing boilers (primary equipment only)
| Demand Control Ventilation++ | 1 | 0 | 0 | 0 | 0 |  |  | 0 |  | Valid for cooling, hydronic boilers (primary or secondary), resistance in AHU.
| Economizer Control - Dry Bulb or Dual Enthalpy | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | Valid for cooling
| Reset Supply Air Discharge Temperature++ | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | Valid for cooling, hydronic boilers (primary or secondary), resistance in AHU.
| Reset Condenser Water Temperature | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | Valid when chiller used
Additional Optimization (Subscription Based System Control Products) - The below fields may be used to account for additional optimization strategies employed by subscription based system control products that are not captured in the above sequence list. Optimization sequence eligibility will be determined during MTAC review.
| Cooling System | 0 | 0 | 0 | 0 | 0 | Section of inputs used only for subscription based system controls products only. Eligibility for these sequences is determined by MTAC during product review.
| Ventilation System | 0 | 0 | 0 | 0 | 0
| Heating System | 0 | 0 | 0 | 0 | 0
Sequence Count for Incentive - The following sequence counts are used to calculate incentives. Sequences that provide heating and cooling/ventilation savings are eligible for two Sequence Counts towards the incentive.
| Cooling or Ventilation Saving Sequences | 0 | 0 | 0 | 0 | 0 | Tally of Sequence Count eligible for incentives based on provided project equipment and sequences implemented.
| Heating Saving Sequences | 0 | 0 | 0 | 0 | 0
| Total Sequence Count for Incentive | 0 | 0 | 0 | 0 | 0
Results and Incentives - All Incentives subject to Program Administrator approval and modification. Incentives are capped at 60% of project costs.
|  | Value |  |  |  |  | Messages
| Energy Efficiency Savings | Total | Installation of New BMS | Upgrade of Existing BMS | Subscription Based System Control | Building Control and ADR Enrollment Incentive
| Annual Electric (kWh) | #N/A | #N/A | #N/A | #N/A
| Summer Peak Demand (kW) | #N/A | #N/A | #N/A | #N/A
| Winter Peak Demand (kW) | #N/A | #N/A | #N/A | #N/A
| Annual Fuel Savings (-) | 0 | 0 | 0 | 0
| Incentives | [7 empty] | Indicator | Logic | Messages
| Electric PA Incentive Estimate | #N/A | Missing Data | Missing Data | Missing Data | #N/A | Provide required project information. |  | #N/A | if DR requested but only 1 SOO selected = 0 | Project must include two Cooling or Ventilation Savings Sequences to be eligible for the Demand Response Kicker.
| Gas PA Incentive Estimate | 0 | Missing Data | Missing Data | Missing Data |  |  |  | #N/A | if incentive is calculated, but the eligible incentive differs from calculated incentive = 1 (cap is triggered) | Note that calculated energy efficiency incentive exceeds 60% of project costs and has been capped.
| Total Offer Estimate | #N/A | [6 empty] | 1 | if incentive is not calculated, missing project data | Provide required project information for incentive estimate.
| Other Results | [7 empty] | 0 | if building size outside eligible range, hide incentives | Building is not eligible for incentives based on provided building area.
| Total Project Area Affected (sqft) | 0
| Estimated annual kWh use for affected area (kWh) | 0
| Estimated annual fuel use for affected area (-) | 0
| % kWh Savings of total kWh usage | Missing Data | [6 empty] | #N/A | Hide Results
| % fuel savings of total fuel usage | Missing Data
| Gallons Delivered Fuel Savings (Gal) | Missing Data
| Total Project Costs | #N/A
| Percent of Project Cost Incentivized | Missing Data
Feedback on Missing Results
| Errors | Active Issue | Suggested Action |  |  |  | Jump to section
Eligibility Issues
| Building Area out of Eligible Range | 0 | Consider apply for a custom incentive |  |  |  | Building Energy Use Intensity
| Not eligible for Demand Response Curtailment | #N/A | Select at least two unique electric energy savings sequences |  |  |  | Project Information
| Product has not been reviewed by MTAC | #N/A | Submit product for review prior to application for incentives |  |  |  | Control System Information
Data Entry Issues
| EUI cannot be calculated | 1 | Provide building area and consumption in the Building Energy Use Intensity section |  |  |  | Building Energy Use Intensity
| Control Area exceeds Building Area | 0 | Ensure that project areas do not overlap |  |  |  | Project Information
| Missing Installation Cost | #N/A | Provide project cost estimates |  |  |  | Control System Information
Jump to Top
Results and Incentives by Project Area - All Incentives subject to Program Administrator approval and modification. Incentives are capped at 60% of project costs. This table excludes the DR enrollment incentives
|  | Results |  |  |  |  | Messages
Results by Area - The totals here match the total results, but are presented by area
|  | Area 1 | Area 2 | Area 3 | Area 4 | Area 5 | Total Project
| Annual Electric (kWh) | 0 | 0 | 0 | 0 | 0 | 0
| Summer Peak Demand (kW) | 0 | 0 | 0 | 0 | 0 | 0
| Winter Peak Demand (kW) | 0 | 0 | 0 | 0 | 0 | 0
| Annual Fuel Savings (-) | #N/A | 0 | 0 | 0 | 0 | #N/A
| Electric PA Incentive Estimate | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Gas PA Incentive Estimate | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## Equipment and SOO (hidden)
Equipment and SOO Eligibility
This table summarizes what sequences are eligible on what types of equipment
The equipment and labeling here are used elsewhere in the tool in lookups and drop down menus. All labeling should match to ensure lookups work properly.
| Equipment |  |  |  | section not used - left in place so I don’t disrupt the column references |  |  |  | Savings Reference |  | Standard BMS SOO | [8 empty] | RCx Activity
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 15 | 16 | 17 | 18
| Equipment Category | Type | reference | unique | Table ref for primary heat drop down | table ref for Vent drop down | table ref for terminal unit drop down | table ref for cooling drop down | For heating - Relative efficiency compared to non-condensing boiler. For other - reference to savings to be used | Estimate of electric heat as % of building electric load | System Schedules and Unoccupied Setbacks++ | Optimal Start / Stop++ | Reset Chilled Water Temperature | Reset Static Pressure | Reset Boiler Water Temperature | Demand Control Ventilation++ | Economizer Control - Dry Bulb or Dual Enthalpy | Reset Supply Air Discharge Temperature++ | Reset Condenser Water Temperature | Reduce over ventilation | Reduce Simultaneous heating and cooling - Leaking Valve | Reduce Simultaneous heating and cooling - Temperature Setpoints | Reduce Steam Pressure | Notes
1 | Primary Heating Type | Steam Boiler | 1 | ph1 |  |  |  |  | 1.0933 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0
2 | ph | Non-Condensing Boiler | 2 | ph2 |  |  |  |  | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0
3 |  | Condensing Boiler | 3 | ph3 |  |  |  |  | 0.8913 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0
4 |  | Furnace or Gas Heat in Air Handler | 4 | ph4 |  |  |  |  | 0.8913 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0
5 |  | Electric Resistance in Air Handler | 5 | ph5 |  |  |  |  | 0.82 | 0.2099 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0
6 |  | Electric Resistance in Terminal Units | 6 | ph6 |  |  |  |  | 0.82 | 0.2099 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 |  | Direct Expansion (ASHP, VRF, GSHP, AWHP) | 7 | ph7 |  |  |  |  | 0.27333 | 0.12403 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
9 |  | N/A or Not Controlled in Project | 0 | ph0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | Central Cooling Type | N/A or Not Controlled in Project | 0 | cc0 |  |  |  |  | eq0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | cc | Direct Expansion (AC, ASHP, VRF, GSHP, AWHP) | 1 | cc1 |  |  |  |  | cc1 |  | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0
14 |  | Chiller | 2 | cc2 |  |  |  |  | cc2 |  | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1
15 | Ventilation | CV Air Handler | 1 | ah1 |  |  |  |  | ah1 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | ah | VAV Air Handler | 2 | ah2 |  |  |  |  | ah2 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0
|  | CV DOAS | 3 | ah3 |  |  |  |  | ah1 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | VAV DOAS | 4 | ah4 |  |  |  |  | ah2 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0
17 |  | Decentralized Ventilation (Unit ventilator) | 5 | ah5 |  |  |  |  | ah2 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 |  | N/A or Not Controlled in Project | 0 | ah0 |  |  |  |  | eq0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | Back Up Heating Type (just for HP) | N/A or Not Controlled in Project | 0 | bh0 |  |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | bh | Steam Boiler | 1 | bh1 |  |  |  |  | 1.0933 |  | 1 |  | 0 | 0 | 0 | 1 | 0 | 1 | 0
21 |  | Non-Condensing Boiler | 2 | bh2 |  |  |  |  | 1 |  | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0
22 |  | Condensing Boiler | 3 | bh3 |  |  |  |  | 0.8913 |  | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0
23 |  | Furnace or Gas Heat in Air Handler | 4 | bh4 |  |  |  |  | 0.8913 |  | 1 |  | 0 | 0 | 0 | 1 | 0 | 1 | 0
24 |  | Electric Resistance in Air Handler | 5 | bh5 |  |  |  |  | 0.82 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | electric back up to HP assumed to be emergency use only. No significant savings on any sequence
25 |  | Electric Baseboard/Cabinet Heater | 6 | bh6 |  |  |  |  | 0.82 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | electric back up to HP assumed to be emergency use only. No significant savings on any sequence
26 | Terminal Units | N/A or Not Controlled in Project | 0 | tu0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | we are including the Tus list here, but will provide incentives based on the major equipment, not this list. Therefore all of these have "0"
27 | tu | Unit Ventilator | 1 | tu1 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 |  | Air Conditioner (PTAC or AC) | 2 | tu2 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 |  | Packaged Terminal Heat Pump (PTHP) | 3 | tu3 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 |  | Fan Powered Terminal Boxes (FPTB) | 4 | tu4 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 |  | CV Box | 5 | tu5 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 |  | VAV Box | 6 | tu6 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Fan Coil Unit (FCU) | 7 | tu7 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Baseboard, Cabinet Heater or Radiators | 8 | tu8 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | VRF or ASHP | 9 | tu9 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 |  | Water Loop Heat Pump | 10 | tu10 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Theoretical Savings
|  |  | Theoretical Savings - link to hidden tabs | section not used - left in place so I don’t disrupt the column references 5: Occ Adjustments
| Heating or Cooling |  | DX or HP | 1: Chiller; section not used - left in place so I don’t disrupt the column references 4: Non-condensing boiler; Standard BMS SOO 10: hard coded value
| Ventilation |  |  | section not used - left in place so I don’t disrupt the column references 2: CV Air Handler; section not used - left in place so I don’t disrupt the column references 3: VAV Air handler; Standard BMS SOO 10: link to theoretical savings tab; Standard BMS SOO 15: Assumptions for expanding the savings allocation beyond theoretical equipment list
1 | Ref | eq0 | cc1 | 1: cc2; section not used - left in place so I don’t disrupt the column references 2: ah1; section not used - left in place so I don’t disrupt the column references 3: ah2; section not used - left in place so I don’t disrupt the column references 5: 0; Savings Reference 6: 7day; Savings Reference 7: 5day; Standard BMS SOO 10: link to assumptions tab; Standard BMS SOO 16: If no mechanical ventilation identified or not included in project - take average cooling savings from where ventilation is included. No theoretical difference in the cooling savings, although the allocated cooling differ between VAV and CV in this tool.
2 | System Schedules and Unoccupied Setbacks++ | 0 |  | section not used - left in place so I don’t disrupt the column references 2: 0.93895; section not used - left in place so I don’t disrupt the column references 3: 0.15605; section not used - left in place so I don’t disrupt the column references 4: 18.9972; section not used - left in place so I don’t disrupt the column references 5: 0; Savings Reference 6: 0.71429; Savings Reference 7: 1; Standard BMS SOO 10: lookup value linked to other tabs; Standard BMS SOO 16: unit vents usually have ECM, so set the savings equal to VAV
3 | Optimal Start / Stop++ | 0 |  | section not used - left in place so I don’t disrupt the column references 2: 0.039153; section not used - left in place so I don’t disrupt the column references 3: 0.039153; section not used - left in place so I don’t disrupt the column references 4: 2.0151; section not used - left in place so I don’t disrupt the column references 5: 0; Savings Reference 6: 0.71429; Savings Reference 7: 1; Standard BMS SOO 10: used as a core reference table elsewhere; Standard BMS SOO 16: assuming DOAS and AHU have same savings, varied by VAV vs CV
4 | Reset Chilled Water Temperature | 0 |  | 1: 0.029677; section not used - left in place so I don’t disrupt the column references 5: 1.4; Savings Reference 6: 1.4; Savings Reference 7: 1; Standard BMS SOO 16: HP savings = DX savings = VRF savings
5 | Reset Static Pressure | 0 |  | section not used - left in place so I don’t disrupt the column references 3: 0.046935; section not used - left in place so I don’t disrupt the column references 5: 1.4; Savings Reference 6: 1.4; Savings Reference 7: 1
6 | Reset Boiler Water Temperature | 0 |  | section not used - left in place so I don’t disrupt the column references 4: 0.73329; section not used - left in place so I don’t disrupt the column references 5: 1.4; Savings Reference 6: 1.4; Savings Reference 7: 1
7 | Demand Control Ventilation++ | 0 | 0.04905 | 1: 0.04905; section not used - left in place so I don’t disrupt the column references 4: 0.80326; section not used - left in place so I don’t disrupt the column references 5: 1.4; Savings Reference 6: 1.4; Savings Reference 7: 1
8 | Economizer Control - Dry Bulb or Dual Enthalpy | 0 | 0.1617 | 1: 0.1617; section not used - left in place so I don’t disrupt the column references 5: 1.4; Savings Reference 6: 1.4; Savings Reference 7: 1
9 | Reset Supply Air Discharge Temperature++ | 0 | 0.00039762 | 1: 0.00039762; section not used - left in place so I don’t disrupt the column references 4: 0.296; section not used - left in place so I don’t disrupt the column references 5: 1.4; Savings Reference 6: 1.4; Savings Reference 7: 1
10 | Reset Condenser Water Temperature | 0 |  | 1: 0.10222; section not used - left in place so I don’t disrupt the column references 5: 1.4; Savings Reference 6: 1.4; Savings Reference 7: 1
11 | Total | 0 | 0.21115 | 1: 0.34305; section not used - left in place so I don’t disrupt the column references 2: 0.9781; section not used - left in place so I don’t disrupt the column references 3: 0.24214; section not used - left in place so I don’t disrupt the column references 4: 22.8449
| Units |  | kWh/sqft | 1: kWh/sqft; section not used - left in place so I don’t disrupt the column references 2: kWh/sqft; section not used - left in place so I don’t disrupt the column references 3: kWh/sqft; section not used - left in place so I don’t disrupt the column references 4: kBtu/sqft
| Explanation |  | Starting (non-condensing boiler, cooling, fans/pumps) theoretical savings taken from green tabs. Represent maximum theoretical savings for each sequence for a "typical" building. Theoretical savings represent the weights that will be used to distribute the Building Level % Saving across the sequences for different combinations of equipment. | bar: 1 to Savings Reference 7
Percent Cooling vs. ventilation
Proportion of ventilation theoretical savings for combinations of equipment
|  |  |  | CV | VAV
|  |  | Dx | 1: 82.25%; section not used - left in place so I don’t disrupt the column references 2: 53.42%
|  |  | Chiller | 1: 74.03%; section not used - left in place so I don’t disrupt the column references 2: 41.38%
|  |  | average | 1: 78.14%; section not used - left in place so I don’t disrupt the column references 2: 47.4%; section not used - left in place so I don’t disrupt the column references 3: 62.77%; section not used - left in place so I don’t disrupt the column references 4: average savings attributed to ventilation
Proportion of cooling theoretical savings for combinations of equipment
|  |  |  | CV | VAV | average
|  |  | Dx | 1: 17.75%; section not used - left in place so I don’t disrupt the column references 2: 46.58%; section not used - left in place so I don’t disrupt the column references 3: 32.17%
|  |  | Chiller | 1: 25.97%; section not used - left in place so I don’t disrupt the column references 2: 58.62%; section not used - left in place so I don’t disrupt the column references 3: 42.29%
[6 empty] | 37.23% | average savings attributed to cooling
Savings Potential
Savings potential is derived from billing analysis (see Building Savings tab) with some modifications for buildings with Chillers (+1% potential). If users do not selecte either coolign or ventilation in a particular area, the savings potential will be reduced by the proportion of theoretical ventilation or cooling savings to the total theortical electric savings.
| Project Type | Reference | Fuel | 1: Electric, non-chiller; section not used - left in place so I don’t disrupt the column references 2: Electric, Chiller; section not used - left in place so I don’t disrupt the column references 3: No Cooling equip selected - Vent savings potential only; section not used - left in place so I don’t disrupt the column references 4: No ventilation selected - cooling savings potential; section not used - left in place so I don’t disrupt the column references 5: Notes
| reference |  |  | 1: 1; section not used - left in place so I don’t disrupt the column references 2: 2; section not used - left in place so I don’t disrupt the column references 3: 3; section not used - left in place so I don’t disrupt the column references 4: 4
| Select Project Type | 0 | 0% | bar: 1 to section not used - left in place so I don’t disrupt the column references 2
| Subscription Based System Control | 1 | 7.064% | 1: 11.76%; section not used - left in place so I don’t disrupt the column references 2: 12.76%; section not used - left in place so I don’t disrupt the column references 3: 7.696%; section not used - left in place so I don’t disrupt the column references 4: 4.565%
| Installation of New BMS | 2 | 7.064% | 1: 11.76%; section not used - left in place so I don’t disrupt the column references 2: 12.76%; section not used - left in place so I don’t disrupt the column references 3: 7.696%; section not used - left in place so I don’t disrupt the column references 4: 4.565%
| Upgrade of Existing BMS | 3 | 7.064% | 1: 11.76%; section not used - left in place so I don’t disrupt the column references 2: 12.76%; section not used - left in place so I don’t disrupt the column references 3: 7.696%; section not used - left in place so I don’t disrupt the column references 4: 4.565%
| Mix of BMS Project Type | 4 | 0% | bar: 1 to section not used - left in place so I don’t disrupt the column references 2
Note on J4: Brougher, Whitney: These are used to reference and adjust (for heating) the theoretical savings. The heating adjustments uses the relative efficiency of the system compared to non-condensing boiler (used in the theoretical savings)
Note on K6: Brougher, Whitney: this isn't used anymore. % electric heat applied at the EUI calculation
Note on C22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Remove PTAC, no ventilation. Uvs can do DCV.
Note on C33: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: PTAC Packed terminal AC, CUH- neither have ventilation.

## Project Savings (hidden)
Conversions
| Type | Input | Value | Notes
| Non Electric Heating Fuel |  | #N/A
| Gas conversion - Therm to kBtu | #N/A | 100 | convert all fuels to kBtu for energy analysis - 1 indicates active fuel
| Propane conversion - Gallon to kBtu | #N/A | 91.452 | convert all fuels to kBtu for energy analysis - 1 indicates active fuel
| Oil conversion - Gallon to kBtu | #N/A | 138.5 | convert all fuels to kBtu for energy analysis - 1 indicates active fuel
| Electric conversion - kWh to kBtu |  | 3.412 | convert all fuels to kBtu for energy analysis - 1 indicates active fuel
Project Selections and References
|  |  | Area 1 | Area 2 | Area 3 | Area 4 | Area 5 | Row Notes | Section Notes
| Inputs | Area used | 0 | 0 | 0 | 0 | 0 |  | directly pulled from input tab
| directly from input tab | Non Electric Heating Fuel | 0 | 0 | 0 | 0 | 0
|  | Project Type | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Occupancy | 0 | 7 Day with Unoccupied Nights | 5-6 Day with Unoccupied Nights | 5-6 Day with Unoccupied Nights | 5-6 Day with Unoccupied Nights
|  | Ventilation Type | CV Air Handler | CV DOAS | N/A or Not Controlled in Project | N/A or Not Controlled in Project | N/A or Not Controlled in Project
|  | Terminal Unit Type | N/A or Not Controlled in Project | Fan Coil Unit (FCU) | N/A or Not Controlled in Project | N/A or Not Controlled in Project | N/A or Not Controlled in Project
|  | Primary Heating Type | Condensing Boiler | Direct Expansion (ASHP, VRF, GSHP, AWHP) | N/A or Not Controlled in Project | N/A or Not Controlled in Project | N/A or Not Controlled in Project
|  | Cooling | Direct Expansion (AC, ASHP, VRF, GSHP, AWHP) | Direct Expansion (AC, ASHP, VRF, GSHP, AWHP) | N/A or Not Controlled in Project | N/A or Not Controlled in Project | N/A or Not Controlled in Project
|  | Secondary Heating Type | N/A or Not Controlled in Project | N/A or Not Controlled in Project | N/A or Not Controlled in Project | N/A or Not Controlled in Project | N/A or Not Controlled in Project
| References for selected equipment | Non Electric Heating Fuel | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Project Type | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Electric heat | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 if electric heat
|  | Occupancy | #N/A | 7day | 5day | 5day | 5day
|  | Ventilation Type | ah1 | ah3 | ah0 | ah0 | ah0
|  | Terminal units | tu0 | tu7 | tu0 | tu0 | tu0
|  | Primary Heating Type | ph3 | ph7 | ph0 | ph0 | ph0
|  | Cooling | cc1 | cc1 | cc0 | cc0 | cc0
|  | cooling and AH code | cc1ah1 | cc1ah3 | cc0ah0 | cc0ah0 | cc0ah0 | NOT USED
|  | back up heating look up | none | bh_HP | none | none | none | back up depends on heating type
|  | Secondary Heating Type | bh0 | bh0 | bh0 | bh0 | bh0
| General Sequence Eligibility | Occupancy check - all | #N/A | 1 | 1 | 1 | 1 | Will be 0 if 24/7 occupancy or if HP heating 7 day | special checks |  | 1
| indicates if sequence eligible on any equipment listed | Occupancy check - HP heating | #N/A | 0 | 1 | 1 | 1 | 1 unless it's a HP @ 7 days, which will not be eligible for scheduling- used in project kBtu calc. No HP heating with 7 day schedule, but still savings on pumps and fans.
| 1=eligible | Ventilation check | 1 | 1 | 0 | 0 | 0 | 0 if no ventilation selected
|  | Back up heating check | 1 | 1 | 1 | 1 | 1 | 0 for back up hydronic boilers, 1 otherwise. Used to zero hydronic boiler savings when used as back up
| sequences | System Schedules and Unoccupied Setbacks++ | #N/A | 1 | 0 | 0 | 0 | not adjusted right now for HP occupancy | Note if SOO is eligible given selected equipment. Used for conditional formatting of sequences in each area on input. NOT DIRECTLY USED IN SAVINGS CALCS DCV, DEEC, and DAT reset only eligible when ventilation selected
|  | Optimal Start / Stop++ | #N/A | 1 | 0 | 0 | 0 | not adjusted right now for HP occupancy
|  | Reset Chilled Water Temperature | 0 | 0 | 0 | 0 | 0 | Valid when chiller used
|  | Reset Static Pressure | 0 | 0 | 0 | 0 | 0 | Valid when VAV selected
|  | Reset Boiler Water Temperature | 1 | 0 | 0 | 0 | 0 | Valid for condensing and non-condensing boilers (primary equipment only)
|  | Demand Control Ventilation++ | 1 | 1 | 0 | 0 | 0 | Valid for cooling, boilers (primary or secondary), resistance in AHU.
|  | Economizer Control - Dry Bulb or Dual Enthalpy | 1 | 1 | 0 | 0 | 0 | Valid for cooling
|  | Reset Supply Air Discharge Temperature++ | 1 | 1 | 0 | 0 | 0 | Valid for cooling, boilers (primary or secondary), resistance in AHU.
|  | Reset Condenser Water Temperature | 0 | 0 | 0 | 0 | 0 | Valid when chiller used
EUI and Savings Potential - Project Area and Building
| Category | Type | Area 1 | Area 2 | Area 3 | Area 4 | Area 5 | Total Project Area | Building | units | Notes
| Project Area Weight | project area sqft | 0 | 0 | 0 | 0 | 0 | 0 | 0 | sqft
|  | % of building area represented | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | %
| Consumption in Area | Electric Consumption | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | kBtu
|  | Fuel Consumption | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | kBtu | any fuel consumption converted to kBtu. spaces with electric heating should have less gas use, but that's beyond the function of the tool currently. Assumed no change in gas use.
|  | Total Consumption | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | kBtu
|  | Electric Heat | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | kBtu | Logic here - if electric resistance (in AHU or baseboard) - 21% of electric for heating. If HP 12%
|  | Electric Non-heat | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | kBtu
| EUI by Area | Electric EUI | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | kBtu/sqft
|  | Fuel EUI | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | kBtu/sqft
|  | Total EUI | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | kBtu/sqft
|  | Electric Heat EUI | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | kBtu/sqft
|  | Electric Non-heat EUI | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | kBtu/sqft
| Building Savings Potential | Building Savings Potential set | 1 | 1 | 4 | 4 | 4 |  |  |  | reference based on the equipment savings (chiller, non chiller, cooling only, ventilation only) that will determine the total building savings potential
|  | Electric Cooling and Ventilation | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | % | look up also allows for savings potential to change by project type, but right now the savings are all equivalent
|  | Electric Heating | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | %
|  | Fuel Heating | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | %
SOO % Allocation Values |  |  | vlookup (of the SOO and the equipment in area) % allocation
These values represent the % of the savings potential avilable to each sequence in each area given the selected equipment. This does not reflect building savings potential, but the share of the building savings potential attributed to each SOO based on theoretical savings. This calculates the % allocation based on teh appropriate theoretical savings and applies the SOO eligibility
| Type |  | Area 1 | Area 2 | Area 3 | Area 4 | Area 5 | Total | Notes
| Reference for Theoretical Savings | Cooling Set | cc1 | cc1 | eq0 | eq0 | eq0 |  | theoretical savings developed for chiller and DX only. These are used as basis for savings for other equipment (see Equipment and SOO tab)
|  | Ventilation set | ah1 | ah1 | eq0 | eq0 | eq0 |  | theoretical savings developed for CV and VAV Air Handlers only. These are used as basis for savings for other equipment (see Equipment and SOO tab)
|  | Primary Heating - relative to non-cond | 89.13% | 27.33% | 0% | 0% | 0% |  | this is relative efficiency of selected system vs. non-condensing boiler (foundation of theoretical savings)
|  | Secondary Heating - relative to non-cond | 0% | 0% | 0% | 0% | 0% |  | this is relative efficiency of selected system vs. non-condensing boiler (foundation of theoretical savings)
2 | Cooling and Ventilation Savings | System Schedules and Unoccupied Setbacks++ | 78.95% | 78.95% | 0% | 0% | 0% | 1.5791 |  | 0.9781
3 |  | Optimal Start / Stop++ | 3.292% | 3.292% | 0% | 0% | 0% | 0.065845
4 |  | Reset Chilled Water Temperature | 0% | 0% | 0% | 0% | 0% | 0
5 |  | Reset Static Pressure | 0% | 0% | 0% | 0% | 0% | 0
6 |  | Reset Boiler Water Temperature | 0% | 0% | 0% | 0% | 0% | 0
7 |  | Demand Control Ventilation++ | 4.124% | 4.124% | 0% | 0% | 0% | 0.082489
8 |  | Economizer Control - Dry Bulb or Dual Enthalpy | 13.6% | 13.6% | 0% | 0% | 0% | 0.27194
9 |  | Reset Supply Air Discharge Temperature++ | 0.03343% | 0.03343% | 0% | 0% | 0% | 0.00066869
10 |  | Reset Condenser Water Temperature | 0% | 0% | 0% | 0% | 0% | 0 |  |  |  | The % Building savings for each sequence is determined by allocating the total building savings potential across the eligible system sequences. * In cases where building has electric heating, the % savings from this table are applied to the electric heating estimate, not to the full building consumption. Notes on back up heat: * back up heating systems aren't eligible for OSS or HW reset. * FF back up system - no adjustments made to % building savings - we're assuming that the gas consumption will be proportionally lower and account for switchover temperatures used on site * Electric back up system - assuming no one is doing a switchover control from a HP to electric resistance and that it's only in place for emergency. No savings attributed.
2 | Electric Heating Savings | System Schedules and Unoccupied Setbacks++ | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
3 |  | Optimal Start / Stop++ | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
4 |  | Reset Chilled Water Temperature | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
5 |  | Reset Static Pressure | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
6 |  | Reset Boiler Water Temperature | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
7 |  | Demand Control Ventilation++ | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
8 |  | Economizer Control - Dry Bulb or Dual Enthalpy | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
9 |  | Reset Supply Air Discharge Temperature++ | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
10 |  | Reset Condenser Water Temperature | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
2 | Fuel Heating Savings | System Schedules and Unoccupied Setbacks++ | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
3 |  | Optimal Start / Stop++ | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
4 |  | Reset Chilled Water Temperature | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
5 |  | Reset Static Pressure | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
6 |  | Reset Boiler Water Temperature | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
7 |  | Demand Control Ventilation++ | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
8 |  | Economizer Control - Dry Bulb or Dual Enthalpy | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
9 |  | Reset Supply Air Discharge Temperature++ | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
10 |  | Reset Condenser Water Temperature | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Project Savings - kBtu
% building savins * area EUI * user selection in area * affected area * % allocation * occ adjustment (of SOO and the occ schedule adjustment) * Ventilation adjustment (for DCV, DEEC, DAT reset - will zero out when no ventilation)
| Type |  | Area 1 | Area 2 | Area 3 | Area 4 | Area 5 | Total | Notes
2 | Cooling and Ventilation Savings | System Schedules and Unoccupied Setbacks++ | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | ventilation
3 |  | Optimal Start / Stop++ | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | ventilation
4 |  | Reset Chilled Water Temperature | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | cooling
5 |  | Reset Static Pressure | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | ventilation
6 |  | Reset Boiler Water Temperature | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | N/A
7 |  | Demand Control Ventilation++ | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | cooling. NOTE INCLUDES VENTILATION CHECK ROW 33
8 |  | Economizer Control - Dry Bulb or Dual Enthalpy | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | cooling. NOTE INCLUDES VENTILATION CHECK ROW 34
9 |  | Reset Supply Air Discharge Temperature++ | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | cooling. NOTE INCLUDES VENTILATION CHECK ROW 34
10 |  | Reset Condenser Water Temperature | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | cooling
2 | Electric Heating Savings | System Schedules and Unoccupied Setbacks++ | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | this is where HP heating at 7 days falls out
3 |  | Optimal Start / Stop++ | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
4 |  | Reset Chilled Water Temperature | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
5 |  | Reset Static Pressure | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
6 |  | Reset Boiler Water Temperature | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7 |  | Demand Control Ventilation++ | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | NOTE INCLUDES VENTILATION CHECK ROW 33
8 |  | Economizer Control - Dry Bulb or Dual Enthalpy | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | NOTE INCLUDES VENTILATION CHECK ROW 33
9 |  | Reset Supply Air Discharge Temperature++ | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | NOTE INCLUDES VENTILATION CHECK ROW 33
10 |  | Reset Condenser Water Temperature | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | Fuel Heating Savings | System Schedules and Unoccupied Setbacks++ | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
3 |  | Optimal Start / Stop++ | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
4 |  | Reset Chilled Water Temperature | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
5 |  | Reset Static Pressure | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
6 |  | Reset Boiler Water Temperature | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7 |  | Demand Control Ventilation++ | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | NOTE INCLUDES VENTILATION CHECK ROW 33
8 |  | Economizer Control - Dry Bulb or Dual Enthalpy | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | NOTE INCLUDES VENTILATION CHECK ROW 33
9 |  | Reset Supply Air Discharge Temperature++ | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | NOTE INCLUDES VENTILATION CHECK ROW 33
10 |  | Reset Condenser Water Temperature | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Subscription Optimization Savings | Cooling | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | These savings are for optimization sequences not accounted for in other eligible SOOs. cooling savings from: CHW reset, DCV, Econ, DAT reset, CW reset
|  | Ventilation | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Heating | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Total by savings type | Cooling and Ventilation | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Electric heating | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | fuel heating | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| SOO Tally for incentives | scheduling - Cooling | 0 | 0 | 0 | 0 | 0 |  | this is used to set incentives. Using a count of sequences that come through with savings, which means the equipment is used, the sequence is eligible, and the user selected the sequence.
|  | scheduling - heating | #N/A | #N/A | #N/A | #N/A | #N/A
|  | # cooling/vent Savings SOO | #N/A | #N/A | #N/A | #N/A | #N/A |  | includes optimization and regular EE
|  | # heating Savings SOO | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Total | #N/A | #N/A | #N/A | #N/A | #N/A |  | this is used to set incentives. Using a count of sequences that come through with savings, which means the equipment is used, the sequence is eligible, and the user selected the sequence.
| Savings Totals by Energy Type | Electric | 0 | 0 | 0 | 0 | 0 | 0
|  | Electric for kW consideration | 0 | 0 | 0 | 0 | 0 | 0
|  | Fuel | 0 | 0 | 0 | 0 | 0 | 0
|  | Total | 0 | 0 | 0 | 0 | 0 | 0
Project Savings - Final Units
| Savings Totals by Energy Type - kWh and Therm Units | Electric (kWh) | 0 | 0 | 0 | 0 | 0 |  | These are used to populat a tab that summarizes the project. Intent is to copy that into a consolidated spreadsheet to do analysis across projects.
Electric for kW consideration
|  | Fuel (therms) | #N/A | #N/A | #N/A | #N/A | #N/A
Total
| Savings by Area and Final Units | Annual Electric (kWh) | 0
|  | Electric kWh for kW considerations | 0
|  | Summer Peak Demand (kW) | 0
|  | Winter Peak Demand (kW) | 0
|  | Gas Therms | #N/A
|  | Oil MMBtu | #N/A
|  | Propane MMBtu | #N/A
|  | Annual Fuel Savings (Therms gas or MMBtu delivered) | #N/A
Electric PA Incentive Estimate
Gas PA Incentive Estimate
Incentive Count - Sequence Tally
| Type |  | Area 1 | Area 2 | Area 3 | Area 4 | Area 5
|  | System Schedules and Unoccupied Setbacks++ | 0 | 0 | 0 | 0 | 0
|  | Optimal Start / Stop++ | 0 | 0 | 0 | 0 | 0
|  | Reset Chilled Water Temperature | 0 | 0 | 0 | 0 | 0
|  | Reset Static Pressure | 0 | 0 | 0 | 0 | 0
|  | Reset Boiler Water Temperature | 0 | 0 | 0 | 0 | 0
|  | Demand Control Ventilation++ | 0 | 0 | 0 | 0 | 0
|  | Economizer Control - Dry Bulb or Dual Enthalpy | 0 | 0 | 0 | 0 | 0
|  | Reset Supply Air Discharge Temperature++ | 0 | 0 | 0 | 0 | 0
|  | Reset Condenser Water Temperature | 0 | 0 | 0 | 0 | 0
|  | Total | 0 | 0 | 0 | 0 | 0
Reported Annual Savings - All zeroed out if missing key information or errors
| Fuel | Savings Type | Installation of New Traditional BMS | Upgrade of Traditional BMS | Subscription Based Control | Total | Unit | Notes
|  | ref # -> | 2 | 3 | 1
| Electric | Annual kWh | 0 | 0 | 0 | 0 | kWh
|  | kWh Considered for Peak Demand | 0 | 0 | 0 | 0 | kWh
|  | Summer Peak kW | 0 | 0 | 0 | 0 | kW | Updated for 2025 using kWh Conversion factor approach used in the BC model. Uses total annual kWh savings rather than excluding schedule and OSS
|  | Winter Peak kW | 0 | 0 | 0 | 0 | kW | Updated for 2025 using kWh Conversion factor approach used in the BC model. Uses total annual kWh savings rather than excluding schedule and OSS
| Fossil Fuel | Gas Energy | #N/A | #N/A | #N/A | #N/A | Therms
|  | Propane Energy | #N/A | #N/A | #N/A | #N/A | MMBtu
|  | Oil Energy | #N/A | #N/A | #N/A | #N/A | MMBtu
|  | Propane Gal | #N/A | #N/A | #N/A | #N/A | Gallon
|  | Oil Gal | #N/A | #N/A | #N/A | #N/A | Gallon

## Incentive Calc (hidden)
Incentive Info | [12 empty] | electric | gas
|  | Type | Reference | non scheduling | Scheduling | Measure Life | Notes |  | ADR Kicker |  |  | System Schedules and Unoccupied Setbacks++ | 1 | 1 | both
| Rates | Demand Response |  | 500 |  |  |  |  | 3000 | > 1.5 milliion kWh |  | Optimal Start / Stop++ | 1 | 1 | both
|  | Base Rate - Subscription |  | 0.01 |  |  |  |  | 500 | <= 1.5 million kWh
|  | Base Rate - BMS |  | 0.1 | [7 empty] | Reset Chilled Water Temperature |  | 1
| Multipliers | Installation of New BMS | 2 | 1 | 1 | 15 | [5 empty] | Reset Static Pressure |  | 1
|  | Upgrade of Existing BMS | 3 | 0.5 | 0.5 | 5 | [5 empty] | Reset Boiler Water Temperature | 1
|  | Subscription Based System Control | 1 | 0.5 | 1 | 5 | non-scheduling - multiplier is 0.3 * # years. Scheduling - to allow higher incentive for first year installation, which we think will provide offline scheduline on site for ML of new BMS, we will use the BMS multiplier if this project includes scheduling and is first year hardware installation. otherwise scheduling has normal subscription rate. |  |  |  |  | Demand Control Ventilation++ | 1 | 1
| Cap | Total Project Cost |  | 60% | [7 empty] | Economizer Control - Dry Bulb or Dual Enthalpy |  | 1
[12 empty] | Reset Supply Air Discharge Temperature++ | 1 | 1
Area Calculations - Energy Incentives | [11 empty] | Reset Condenser Water Temperature |  | 1
|  | Project Area | lookup column | Area 1 | Area 2 | Area 3 | Area 4 | Area 5 | Total | Units | Notes
| Project Type |  |  | #N/A | #N/A | #N/A | #N/A | #N/A
| Eligible SOO | Scheduling - cooling/ventilation |  | 0 | 0 | 0 | 0 | 0 |  |  | ADR kicker logic based on selection and use of 2 energy SOO | Subscription Based System Control | 1
|  | Scheduling - heating |  | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | Installation of New BMS | 2
|  | Cooling/ventilation |  | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | Upgrade of Existing BMS | 3
|  | Heating |  | #N/A | #N/A | #N/A | #N/A | #N/A
|  | ADR | [6 empty] | #N/A
|  | Total |  | 0 | 0 | 0 | 0 | 0
| Incentive - Traditional BMS | Incentive Rate | 3 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | based on project type look up the incentive rate
|  | $/sqft |  | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Total Area Incentive |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Incentive - Subscription | Non-scheduling rate |  | #N/A | #N/A | #N/A | #N/A | #N/A
|  | scheduling rate |  | #N/A | #N/A | #N/A | #N/A | #N/A
|  | $/sqft - non schedule |  | #N/A | #N/A | #N/A | #N/A | #N/A
|  | $/sqft - schedule |  | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Total Area Incentive |  | 0 | 0 | 0 | 0 | 0 | 0
| Benchmark EUIs | Electric |  | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Electric Heat |  | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Electric Non-heat |  | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Fuel |  | #N/A | #N/A | #N/A | #N/A | #N/A
| Adjusted Savings | Annual kWh | [6 empty] | 0 | kWh | Savings are adjusted here by multiplying the % savings by the ratio of benchmark to site EUI
|  | kWh Considered for Peak | [6 empty] | 0 | kWh | Not used in 2025
|  | Summer kW | [6 empty] | 0 | kW | Updated in 2025 to use BC model kW calculation using kWh conversion factor and CF
|  | Fuel | [6 empty] | 0 | MMBtu
| Benefits | Measure Life Lookup | 4 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | look up measure life for non subscription products (on tables tab). If subscription, use value from screen
|  | kWh | 2 | [5 empty] | 0 | $ benefit
|  | kW | 3 | [5 empty] | 0 | $ benefit
|  | Gas | 4 | [5 empty] | 0 | $ benefit
|  | Total |  | 0 | 0 | 0 | 0 | 0 | 0 | $ benefit
Project Totals
|  | Type | lookup column | Total | Electric | Gas | Notes
|  | Electric only PA |  |  | #N/A |  | if gas is used, allocate incentive. If gas not used, 100% electric by default
| Total Project | Energy Allocation |  |  | #N/A | #N/A | Allocation based on total energy benefits
|  | Max Incentive |  | #N/A |  |  | Project Cost * 60%
|  | DR readiness |  | #N/A |  |  | DR Kicker if "Yes" selected and 2 electric sequences implemented
|  | Total Calculated Energy Incentive |  | #N/A |  |  | Based on Area Calcs above
|  | Eligible energy Incentive |  | #N/A |  |  | Minimum value between calculated incentive and 60% project costs + DR kicker
|  | Allocated Eligible Incentive |  |  | #N/A | #N/A
|  | Effective allocation (with cap) |  |  | #N/A | #N/A
Incentives by Area
|  |  |  | Area 1 | Area 2 | Area 3 | Area 4 | Area 5 | Total
| Incentive by Area |  | Electric | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  | Gas | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  | DR | [5 empty] | #N/A
|  |  | Total | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Project Type allocation
|  | Project Type | lookup column | Benefits | Allocation of benefits | Total Incentive Allocated | Electric | Gas | Notes
|  | DR Readiness |  |  |  |  | #N/A
|  | Installation of New Traditional BMS | 2 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Upgrade of Existing Traditional BMS | 3 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Subscription Based Controls | 1 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Total |  |  |  | #N/A | #N/A | #DIV/0!
Benefits for % Allocation Estimates
| Benefit Stream | kWh Benefit factor ($/kWh) | Summer kW Benefit factor ($/kW) | Gas Benefit Factor ($/MMBtu)
| 1 | 0.34069 | 226.6509 | 43.5309
| 2 | 0.67887 | 427.5508 | 87.0634
| 3 | 1.0238 | 626.7157 | 129.2608
| 4 | 1.3697 | 872.2907 | 171.1371
| 5 | 1.7105 | 1103.8562 | 212.0423
| 10 | 3.2697 | 2272.7412 | 407.1971
| 15 | 4.5244 | 3409.1765 | 604.694

## PA Only - Pre-Inspection
Legend
| Overview | [5 empty] | User Input
| The pre-inspection form is for PA use. PAs will reach out to schedule a pre-inspection at the facility and complete this form or equivalent during their inspection. | [5 empty] | Project Calculation
Not applicable to project
| Statewide Data Collection | Prescriptive BMS Pre Inspection |  |  | Version N°: | 2026 V1.0
| Company Name: |  |  |  | Version Date: | 2026-01-15
| Company Address: |  | Street | City | Gas PA: | Eversource Gas
| Customer Contact Name: |  | Phone N°: |  | Electric PA: | Eversource
PA Technical Representative:
| PA Technical Representative Phone Number: |  |  | Application #:
Electric accounts associated with the building:
Gas accounts associated with the building:
This prescriptive BMS offer supports installation or optimization of new Building Mangament Systems, upgrades to existing systems, and implimentation of subscription based control products.
| Printable Format? | No
Data Collection
|  | Inputs | Messages or Instruction |  |  |  | Proposed Project Type | Description
| Inspection | [5 empty] | Subscription Based Control | Incentive sought for first time installation of subscription based control product or for renewal of subscription.
| Date of Inspection | [5 empty] | First time BMS installation | Incentive sought for first time installation of a traditional BMS, replacing decentralized control system without trend capabilities.
| Pre-inspector Name/Company | [5 empty] | Legacy System Replacement | Incentive sought to replace an existing BMS. Existing system must be more than 15 years old to be eligible.
| Vendor Name/Company | [5 empty] | Add on of new sequence(s) | Incentive sought to expand existing BMS to control additional existing equipment or impliment a new SOO.
| Customer Name/Company | [5 empty] | Tune up of existing sequence(s) | Incentive sought to optimize existing sequences on an existing BMS.
| Building Information | [5 empty] | Mix of Project Type | Incentives sought for a project that includes partial system replacement with improvements to existing BMS.
| Total Building Area (sqft) |  | May be approximate
Total Heated Area (sqft)
Total Cooled Area (sqft)
| Does the building have renewables or CHP behind the meter? | No | Informational purposes only to facilitate project review.
| Is there a current or planned building renovation? | No | Buildings with the following are not eligible: - Significant process or lab loads - Significant new loads or changes in space use - New buildings, new additions to a building, or buildings participating in the Mass Save New Construction and Major Renovations program. |  |  |  |  | Select from dropdown
| Does the building include labs or process loads? | No
| Notes or explanation on above | [5 empty] | Age Verification Approach | Description
| HVAC Equipment | [5 empty] | Date on field panel | Provide pictures of field panel (s) with date of manufacturer
| Primary Heating Equipment |  |  |  | Provide high level overview of HVAC equipment. Does not require a full equipment inventory. Note any equipment that is new or planned to be replaced as necessary. |  | Model number | If panel age or mechanical control drawings aren't available, provide field panel's full model number.
| Primary Cooling Equipment | [5 empty] | Other | Provide other evidence of system age. May not be accepted by reviewing PA.
Air Handling
Terminal units (for ventilation)
Notes or explanation on above
Existing and Proposed Control
| Proposed Project Type | Legacy System Replacement | Incentive sought to replace an existing BMS. Existing system must be more than 15 years old to be eligible.
| Existing Control System |  | Examples: thermostats, centralized control system (BMS), pneumatic system, local control, mix of systems
| Existing System Manufacturer(s) |  | Examples: Siemens, Johnson
| If known, has the customer previously received program support for the system? | No
If known, approximately when was the previous incentive received?
| Legacy System Replacement - Method of checking existing BMS system age (listed in order of preference) | Date on field panel | Provide pictures of field panel (s) with date of manufacturer
Legacy System Replacement - Age of Existing System based on documentation
Subscription Based System Control - Does the facility have existing hardware required to support proposed subscription controls?
Notes or explanation on above
Documention
Proof of System age
Select from dropdown

## PA Only - MRD Equipment List
| Overview | [12 empty] | Legend
| Provide list of equipment affected by the implimented controls. This list will be used to produce the Project MRD. The MRD lists sequences and verification requirements by equipment. Users may group equipment on the list as long as the group includes the same type of equipment and same implimented sequences. Note - tool does not assess if the selected SOO is appropriate for the listed equipment. For example, equipment described as "Chiller" that has "1" for Reset Boiler Water Temperature will result in a request for hot water setpoints on the chiller. Please review for accuracy. | [12 empty] | User Input
Project Calculation
Not applicable to project
Summary of User Inputs
Summary of sequences selected by Project Area from User Inputs and Savings tab. Provided to assist in populating the Equipment list sequences.
| Control Area | Area Description | Area sqft | System Schedules and Unoccupied Setbacks++ | Optimal Start / Stop++ | Reset Chilled Water Temperature | Reset Static Pressure | Reset Boiler Water Temperature | Demand Control Ventilation++ | Economizer Control - Dry Bulb or Dual Enthalpy | Reset Supply Air Discharge Temperature++ | Reset Condenser Water Temperature | Total # Unique SOO
| Area 1 | 0 | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A
| Area 2 | Retail | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Area 3 | [description 3] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Area 4 | [description 4] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Area 5 | [description 5] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Equipment Information for Project Review
| Will trend data be reviewed for this project? |  |  | Yes | Exclusion of trend data review should be approved by reviewing engineer.
Equipment List - Complete after the "User Inputs and Savings" tab. Used to generate MRD used for post-inspection. Populate with list of affected equpiment, including equipment tag. Mark "1" for sequences affecting listed equipment. Greyed sequences are not eligible and/or included in project scope per the provided user inputs.
| Item # | Equipment Description and Tag(s) | Area(s) served | System Schedules and Unoccupied Setbacks++ | Optimal Start / Stop++ | Reset Chilled Water Temperature | Reset Static Pressure | Reset Boiler Water Temperature | Demand Control Ventilation++ | Economizer Control - Dry Bulb or Dual Enthalpy | Reset Supply Air Discharge Temperature++ | Reset Condenser Water Temperature | Total Sequences Implimented on Equipment
| Example | Chillers 1 and 2 - CHL-1, CHL-2 | Project Areas 2 and 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2
| 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A
| 2 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 9 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 11 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 12 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 13 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 14 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 15 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
The following tables will check if the sequence is used and eligible in the project.
|  |  |  | System Schedules and Unoccupied Setbacks | Optimal Start / Stop | Reset Chilled Water Temperature | Reset Static Pressure | Reset Boiler Water Temperature | Demand Control Ventilation | Economizer Control - Dry Bulb or Dual Enthalpy | Reset Supply Air Discharge Temperature | Reset Condenser Water Temperature
|  | Sequence Used and Eligible |  | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Used in conditional formating above
|  | Trends Required? |  | 1 | if using - 1 = yes, 0 = no. If 0 then all trends will be zeroed out
| Is row used? | Provided description | [10 empty] | Final Text
Trend Requirements | #N/A | #N/A |  | #N/A | #N/A | [7 empty] | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
Screenshot Requirements | #N/A | #N/A |  | #N/A | #N/A | [7 empty] | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
Sequences | #N/A | #N/A |  | #N/A | #N/A | [7 empty] | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A
| FALSE |  |  | #N/A | #N/A

## PA Only - Project MRD
Overview
The Minimum Requirements Document (MRD) will be populated using customer information from the "User Inputs and Savings" tab and equipment from the "MRD Equipment List" tab. Reviewing engineers must ensure that the Equipment List tab and selected sequences are appropriate for the project, reflect provided Sequence of Operation, and align with Inputs tab. Document will print excluding this overview section.
Customer | [6 empty] | Program | Prescriptive BMS
Facility | [6 empty] | Application #:
Measure |  | This prescriptive BMS measure implements new or optimizes energy savings building control seqences at facilities. These facilities may be implementing a new functional BMS on existing equipment, expandingan existing BMS, replacing an older BMS (discuss with Technical Representative for more information), or adding a new system-based subscription control product.
This document specifies the agreed upon minimum equipment specifications and operational requirements of the proposed system. These requirements shall address the criteria necessary to be met to achieve the demand and energy savings estimated in the engineering analysis for this project. Yes/No checkboxes are intended for use as post-installation inspection record (check one).
EQUIPMENT: Provide a list of equipment or materials installed as part of this project. Include equipment counts, HP, kW, efficiency and capacity ratings, rating conditions, location of controls hardware, etc.
|  |  |  | Project Design Intent |  |  | Post Inspection Findings
Yes | q | No | q | 0
SEQUENCES OF OPERATION: Provide a description of equipment operating sequences, setpoints, operating schedules, balancing requirements (flow, velocity, head, etc) or any other required operating parameters. Describe requirements separately.
Yes | q | No | q | #N/A | #N/A
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
DOCUMENTATION: List written documentation required to train, verify, operate, or maintain the equipment being installed or controlled. This may include specification sheets, test reports, construction drawings, etc.
Yes | q | No | q | Final control drawings indicating equipment and final Sequences of Operation |  |  | Not needed at post inspection, but needed for incentive application
Yes | q | No | q | 12 months of billing data for all fuels used on site
Yes | q | No | q | Trend Data Report
Yes | q | No | q | Points List
Yes | q | No | q | Proof of Demand Response Enrollment (if applicable)
Yes | q | No | q | #N/A | #N/A
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
POST INSTALLATION VERIFICATION: Provide a list of controls and monitoring capabilities required to verify proper system operation. Trends should document operational sequences, set points and scheduling of equipment as described in TA Study.
Yes | q | No | q | #N/A | #N/A
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
Yes | q | No | q
OTHER REQUIREMENTS: Describe any requirements for demolition, removal, etc. of existing equipment.
Yes | q | No | q
SIGNATURES: The pre-approved incentive is subject to the PA's POST INSPECTION of final specifications, drawings and operation of the proposed equipment. In the event the proposed system is altered from the above description, notify the Company of the change prior to the equipment purchase and installation as the change in design and operation may impact the available incentive.
The PA signature below indicates the PA engineer, or their representative, has reviewed and agrees to the requirements stated in this MRD. The customer signature below indicates the customer also agrees with the requirements of this MRD and will implement as stated. The customer should only sign below if this MRD has been signed by their PA or their representative.
PA Engineer or Representative |  |  |  |  | Date | Customer Agreement Signature |  |  | Date
Once the installation is complete and the equipment is operational, the post inspector will sign below, confirming all requirements of this MRD have been met, and/or any discrepancies have been noted. The PA will review any discrepancies to determine their impact on energy savings or incentive. The final customer signature indicates that they agree with the findings of the post inspector, including any discrepancies noted, and are satisfied with the installation.
PA Engineer or Representative |  |  |  |  | Date | Customer Agreement Signature |  |  | Date

## Project Notes - Optional
Project Notes
Customer:
Application
User may note any clarifying comments on the project area, implimented sequences, equipment controlled, etc. Notes should be provided to explain any unusual project scenarios or PA feedback on the project.
Notes

## EUI Benchmark
Overview | [7 empty] | Legend
This tab is intended to facilitate project review by providing EUI benchmarks for common building types. Cells D10-D12 will indicate whether consumption exceed benchmarks, and if the user should verify building consumption and other inputs on the "User Inputs and Savings Tab". Project EUI is not required to be within 25% of benchmark, but please review inputs for accuracy in the case of high or low EUIs. | [7 empty] | User Input
Project Calculation
Static
Project EUI Feedback
Select Principle building activity |  | Major Fuels | Electric |  | Fossil Fuel [1]
|  | kbtu/sqft | kwh/sqft | kbtu/sqft | Ccf/sqft | kbtu/sqft
0 |  | 0 | 0 | 0 | N/A | 0
Based on the provided consumption data and building area:
The project Major Fuel EUI is |  | Provide requested project information for feedback.
The project Electric EUI is |  | Provide requested project information for feedback.
The project Fossil Fuel EUI is |  | Provide requested project information for feedback.
[1] EUI displayed in column G represents whatever fossil fuel is used for this project (natural gas, oil, or propane)
Benchmark EUI [2]
Select Principle building activity | Source | Major Fuels | Electric |  | Natural Gas
|  | kbtu/sqft | kwh/sqft | kbtu/sqft | cf/sqft | kbtu/sqft | numbers below used to flag relevant building type
Food sales | [3] | 297.9096 | 40.8 | 139.2096 | 153.0376 | 158.7 | 0
Food service | [4] | 204.4 | 29.7 | 101.3364 | 99.3863 | 103.0636 | 0
Health care - Inpatient | [2] | 190 | 22.4 | 76.4288 | 89.5 | 92.8115 | 0
Other | [2] | 141.2 | 31.4 | 107.1368 | 38.7 | 40.1319 | 0
Health care - Total | [2] | 135.2 | 19 | 64.828 | 58.2 | 60.3534 | 0
Mercantile - Enclosed and strip malls | [2] | 112.1 | 17.9 | 61.0748 | 49.2 | 51.0204 | 0
Lodging | [2] | 92.7 | 13.7 | 46.7444 | 45.7 | 47.3909 | 0
Mercantile - Total | [2] | 88.2 | 15.1 | 51.5212 | 41.9 | 43.4503 | 0
Health care - Outpatient | [2] | 86.5 | 15.9 | 54.2508 | 30.9 | 32.0433 | 0
Public assembly | [2] | 86 | 9.6 | 32.7552 | 52.6 | 54.5462 | 0
Office | [2] | 74.3 | 13.8 | 47.0856 | 20.6 | 21.3622 | 0
Education | [2] | 73.2 | 7.9 | 26.9548 | 41.5 | 43.0355 | 0
Public order and safety | [4] | 58.4 | 9.9941 | 34.1 | 21.8901 | 22.7 | 0
Mercantile - Non-Mall Retail | [2] | 57 | 11.3 | 38.5556 | 25 | 25.925 | 0
Religious worship | [2] | 54.9 | 5.1 | 17.4012 | 33.8 | 35.0506 | 0
Service | [2] | 52.2 | 7.3 | 24.9076 | 38.2 | 39.6134 | 0
Warehouse and storage | [2] | 35 | 6 | 20.472 | 19.3 | 20.0141 | 0
Vacant | [4] | 14.1 | 3.1653 | 10.8 | 3.2787 | 3.4 | 0
[2] Benchmark data is sourced from CBECS (https://www.eia.gov/consumption/commercial/data/2018/index.php?view=consumption): - Table C5: Consumption and gross energy intensity by census region for sum of major fuels, 2018. - Table C15: Electricity consumption and conditional energy intensity by census region, 2018 - Table C25. Natural gas consumption and conditional energy intensity by census region, 2018 Presented data is for the Northeast region and listed by Principal Building Activity. Note that "Major Fuels" includes electricity, natural gas, fuel oil, district heat, district chilled water, propane, solar, wood, coal, and other. 1,037 Btu per cubic foot natural gas used as a conversion factor.
[3] CBECS data not available for Food Service in the Northeast region. Provided EUI values based on National Grid customers. See "2018_cbecs_NE_for_2023_BMS_Calculator.xls" for analysis.
[4] Natural Gas EUI information masked in table C25. Value estimated as Major Fuel EUI minus Electric EUI. See "2018_cbecs_NE_for_2023_BMS_Calculator.xls" for analysis.
This Project - Select PBA* | [6 empty] | 0
Column reference | 3 | 4 | 5 | 6 | 7
Benchmark EUI | #N/A | #N/A | #N/A | #N/A | #N/A
25% higher EUI | #N/A | #N/A | #N/A | #N/A | #N/A
25% lower EUI | #N/A | #N/A | #N/A | #N/A | #N/A
High/Low Flags | Major Fuel | Electric | Fuel
Flag high EUI | #N/A | #N/A | #N/A
Flag low EUI | #N/A | #N/A | #N/A
Any Flag | #N/A | #N/A | #N/A

## for analysis in rows (hidden)
formatting project inputs and results to pull into separate file for project comparisons
[7 empty] | annual consumption |  | Project Sequence Counts | [8 empty] | Optimization |  |  | Savings
index | Project | App | sqft controlled | bld sqft | Project type | Cost | kWh | therm | System Schedules and Unoccupied Setbacks | Optimal Start / Stop | Reset Chilled Water Temperature | Reset Static Pressure | Reset Boiler Water Temperature | Demand Control Ventilation | Economizer Control - Dry Bulb or Dual Enthalpy | Reset Supply Air Discharge Temperature | Reset Condenser Water Temperature | Cooling System | Ventilation System | Heating System | kWh | Therm | Incentive | % Electric Incentive Allocation | Fuel
2 |  |  | 0 | 0 | Mix of BMS Project Type | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
3 |  |  | 0 | 0 | Mix of BMS Project Type | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
4 |  |  | 0 | 0 | Mix of BMS Project Type | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
5 |  |  | 0 | 0 | Mix of BMS Project Type | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
6 |  |  | 0 | 0 | Mix of BMS Project Type | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | 0
|  |  | Select equipment serving each area. If equipment is not eligible (such as new equipment) mark "N/A or Not Controlled in Project". Terminal units not factored into savings or incentives. | 0 | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | 0 | #N/A | #N/A | 0
sequence count for each area and sequence
Area
|  | 1 | 2 | 3 | 4 | 5
| System Schedules and Unoccupied Setbacks | 0 | 0 | 0 | 0 | 0
| Optimal Start / Stop | 0 | 0 | 0 | 0 | 0
| Reset Chilled Water Temperature | 0 | 0 | 0 | 0 | 0
| Reset Static Pressure | 0 | 0 | 0 | 0 | 0
| Reset Boiler Water Temperature | 0 | 0 | 0 | 0 | 0
| Demand Control Ventilation | 0 | 0 | 0 | 0 | 0
| Economizer Control - Dry Bulb or Dual Enthalpy | 0 | 0 | 0 | 0 | 0
| Reset Supply Air Discharge Temperature | 0 | 0 | 0 | 0 | 0
| Reset Condenser Water Temperature | 0 | 0 | 0 | 0 | 0
| Cooling System | 0 | 0 | 0 | 0 | 0
| Ventilation System | 0 | 0 | 0 | 0 | 0
| Heating System | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0

## Tables (hidden)
Tables referenced in drop downs
Drop Down Tables
| Building Schedule | Building Schedule #
| 24/7 Operation | 0 | updated this reference to 0
| 7 Day with Unoccupied Nights | 7day
| 5-6 Day with Unoccupied Nights | 5day
| Heating Fuel |  | Input Units | Result Units | [5 empty] | Subscription Based Control
| Gas | 1 | Therms | Therms | [5 empty] | First time BMS installation
| Propane | 2 | Gallons | MMBtu | [5 empty] | Legacy System Replacement | Incentive sought to replace an existing BMS. Existing system must be more than 15 years old to be eligible.
| Oil | 3 | Gallons | MMBtu | [5 empty] | Add on of new sequence(s) | Incentive sought to expand existing BMS to control additional existing equipment or impliment a new SOO.
| N/A - Electric heating | 0 | N/A | N/A | [5 empty] | Tune up of existing sequence(s) | Incentive sought to optimize existing sequences on an existing BMS.
Mix of Project Type
Project Type
[7 empty] | Select Project Type | 0
[7 empty] | Subscription Based Control | 1 | Incentive sought for first time installation of subscription based control product or for renewal of subscription.
[7 empty] | Installation of New BMS | 2 | Incentive sought for installation of a new traditional BMS. May include replacing decentralized control system without trend capabilities OR replacement of an existing BMS that is over 15 years old. Does not include adding new sequences to an existing BMS.
[7 empty] | Upgrade of Existing BMS | 3 | Incentives sought to optimize existing sequences or add new sequences to an existing traditional BMS
[7 empty] | Mix of Project Type | 4 | Incentives sought for a project that includes partial system replacement with improvements to existing BMS. Project type will be specified in each project area below.
Electric PA List:
National Grid Electric - MA
Eversource
Unitil Electric
Cape Light Compact
None/Default/Muni
Gas PA List:
Eversource Gas
National Grid Gas - MA
NiSource Gas (Columbia Gas)
Berkshire Gas
Unitil Gas
Liberty Gas
None
MRD Requirements by SOO
| Data Verification Requirements | System Schedules and Unoccupied Setbacks | Optimal Start/Stop | Reset Chilled Water Temperature | Supply Air Static Pressure Reset | Reset Boiler Water Temperature | Demand Control Ventilation (DCV) | Economizer Control - Dry Bulb or Dual Enthalpy | Discharge Air Temperature Reset | Reset Condenser Water Temperature
| trends | - Space temperature setpoint(s) - Space temperature(s) for 10% of space - On/Off status of supply fan on each air handler | - On/Off status | - Chilled water supply temperature - Chilled water supply setpoints - Outdoor air temperature | - Discharge static pressure(s) - Static pressure setpoint(s) - Supply fan speed(s) - Virtual calculated feedback point indicating average VAV box damper position OR damper signal of each box associated with air handler | - Hot water supply temperature - Hot water supply setpoints - Outdoor air temperature | - Measured CO2 levels (return air or space(s)) - Outdoor air damper signal - Air handler/room occupancy status | - Outdoor air damper position - Outdoor air temperature (or enthalpy) - Return air temperature (or enthalpy) - Discharge air temperature - Discharge air temperature setpoint - Mixed air temperatures - Cooling valve signal | - Discharge air temperature - Discharge air temperature setpoint - Return air temperature - Outdoor air temperature - Heating status / valve signal - Cooling status / valve signal | - Condenser water supply temperature (leaving chiller) - Condenser water supply temperature setpoint - Outdoor air temperature - Chiller On/Off status - Cooling tower fan On/Off status
| screenshots/other | - Building schedule - Occupied and unoccupied space temperature setpoints | - Building schedule - Major equipment involved with optimal start/stop | - Minimum and maximum chilled water supply temperature setpoints | - Minimum and maximum static pressure setpoints - Boxes associated with each involved air handler | - Minimum and maximum hot water supply setpoints | - Low and high space CO2 thresholds | - No other requirements | - Minimum and maximum discharge temperature setpoints | - Minimum and maximum condenser water supply temperature setpoints
Reference Tables for Drop Downs
drop down references -> the list name is indicated on the Project Savings tab, which is referenced with the indirect function on the data validation list
Text must match the Equipment and SOO exactly!
First equipment selected is ventilation
Drop down populated from the Equipment table list directly
|  |  | How is the space ventilated? | Centralized ventilation | Decentralized ventilation | No Mechanical Ventilation | NA ventilation
| Second equipment selected - TU options based on ventilation selection |  | Ref Table Name | tu_centralized | tu_decentralized | none | TU_full
|  |  | Drop Down values | N/A or Not Controlled in Project | N/A or Not Controlled in Project | N/A or Not Controlled in Project | Unit Ventilator
|  |  |  | Packaged Terminal Heat Pump (PTHP) | Unit Ventilator |  | Air Conditioner (PTAC or AC)
|  |  |  | Fan Powered Terminal Boxes (FPTB) |  |  | Packaged Terminal Heat Pump (PTHP)
|  |  |  | CV Box |  |  | Fan Powered Terminal Boxes (FPTB)
|  |  |  | VAV Box |  |  | CV Box
|  |  |  | Fan Coil Unit (FCU) |  |  | VAV Box
|  |  |  | VRF or ASHP |  |  | Fan Coil Unit (FCU)
|  |  |  | Water Loop Heat Pump |  |  | VRF or ASHP
Water Loop Heat Pump
N/A or Not Controlled in Project
|  |  | Ref Table Name | ph_VRF | ph_WLHP | ph_UV | ph_other | ph_full
| Third equipment selected - primary heating based on TU selection |  | Drop down values | Direct Expansion (ASHP, VRF, GSHP, AWHP) | Non-Condensing Boiler | Steam Boiler | Steam Boiler | Steam Boiler
|  |  |  | N/A or Not Controlled in Project | Condensing Boiler | Non-Condensing Boiler | Non-Condensing Boiler | Non-Condensing Boiler
[5 empty] | Direct Expansion (ASHP, VRF, GSHP, AWHP) | Condensing Boiler | Condensing Boiler | Condensing Boiler
[5 empty] | N/A or Not Controlled in Project | Electric Resistance in Terminal Units | Furnace or Gas Heat in Air Handler | Furnace or Gas Heat in Air Handler
[6 empty] | N/A or Not Controlled in Project | Electric Resistance in Air Handler | Electric Resistance in Air Handler
[7 empty] | Direct Expansion (ASHP, VRF, GSHP, AWHP) | Electric Resistance in Terminal Units
[7 empty] | N/A or Not Controlled in Project | Direct Expansion (ASHP, VRF, GSHP, AWHP)
N/A or Not Controlled in Project
| Final selection - primary cooling based on TU |  | Ref Table Name | cc_VRF | cc
|  |  | Drop down values | Direct Expansion (AC, ASHP, VRF, GSHP, AWHP) | Direct Expansion (AC, ASHP, VRF, GSHP, AWHP)
|  |  |  | N/A or Not Controlled in Project | Chiller
N/A or Not Controlled in Project
|  |  | Primary Heating Selection | Air Source Heat Pump | VRF or VRV System | Water Loop | Other heating
|  |  | Primary Cooling Drop Down | N/A or Not Controlled in Project | N/A or Not Controlled in Project | N/A or Not Controlled in Project | N/A or Not Controlled in Project
|  |  |  | Air Source Heat Pump | VRF or VRV System | Chiller | Direct Expansion (DX)
Chiller
Note on B99: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: PTAC Packed terminal AC, CUH- neither have ventilation.

## Project Verification V1
Project Trend Requirements
Customer:
Application:
Trend data and screenshots are required to verify that implemented sequences align with design expectations. Trends and screenshots must be collected for all major equipment affected by the sequence while the building is operating. Three weeks of trends at 15 to 30 minute intervals must be provided to the Program Administrator in an Excel (.xls) file upon request. All projects must provide a trend report and all requested screenshots as part of the project documentation.
All trends requested subject to program approval and modification. Final trend requirements will be specified and require customer and vendor signature of acknowledgement prior to project approval.
Verification Requirements by Sequence
Sequence | In Project? | Data Requirements
|  | Trends | Screenshots & Other
System Schedules and Unoccupied Setbacks | - | - Space temperature setpoint(s) - Space temperature(s) for 10% of space - On/Off status of supply fan on each air handler | Include noted data points as well as: - Building schedule - Occupied and unoccupied space temperature setpoints | System Schedules and Unoccupied Setbacks | 0
Optimal Start/Stop | - | - On/Off status of major equipment (include as applicable: air handlers, boilers, furnaces, chillers) | Include noted data points as well as: - Building schedule - Major equipment involved with optimal start/stop | Optimal Start / Stop | 0
Reset Chilled Water Temperature | - | - Chilled water supply temperature - Chilled water supply setpoints - Outdoor air temperature | Include noted data points as well as: - Minimum and maximum chilled water supply temperature setpoints | Reset Chilled Water Temperature | 0
Supply Air Static Pressure Reset | - | - Discharge static pressure(s) - Static pressure setpoint(s) - Supply fan speed(s) - Virtual calculated feedback point indicating average VAV box damper position OR damper signal of each box associated with air handler | Include noted data points as well as: - Minimum and maximum static pressure setpoints - Boxes associated with each involved air handler | Reset Static Pressure | 0
Reset Boiler Water Temperature | - | - Hot water supply temperature - Hot water supply setpoints - Outdoor air temperature | Include noted data points as well as: - Minimum and maximum hot water supply setpoints | Reset Boiler Water Temperature | 0
Demand Control Ventilation (DCV) | - | - Measured CO2 levels (return air or space(s)) - Outdoor air damper signal - Air handler/room occupancy status | Include noted data points as well as: - Low and high space CO2 thresholds | Demand Control Ventilation | 0
Economizer Control - Dry Bulb or Dual Enthalpy | - | - Outdoor air damper position - Outdoor air temperature (or enthalpy) - Return air temperature (or enthalpy) - Discharge air temperature - Discharge air temperature setpoint - Mixed air temperatures - Cooling valve signal | Include noted data points | Economizer Control - Dry Bulb or Dual Enthalpy | 0
Discharge Air Temperature Reset | - | - Discharge air temperature - Discharge air temperature setpoint - Return air temperature - Outdoor air temperature - Heating status / valve signal - Cooling status / valve signal | Include noted data points as well as: - Minimum and maximum discharge temperature setpoints | Reset Supply Air Discharge Temperature | 0
Reset Condenser Water Temperature | - | - Condenser water supply temperature (leaving chiller) - Condenser water supply temperature setpoint - Outdoor air temperature - Chiller On/Off status - Cooling tower fan On/Off status | Include noted data points as well as: - Minimum and maximum condenser water supply temperature setpoints | Reset Condenser Water Temperature | 0

## Building Savings (hidden)
Purpose: This table summarizes the billing analysis performed by Mike Mills (Eversource) on past EMS projects. All billing data and projects are pre-covid. Electric consumption is not weather normalized, gas consumption is weather normalized.
|  |  |  | Annual Electric (kWh) |  |  | Annual Gas (therm) |  |  |  |  | Pre Energy Usage Intensity
Project # | Building Type | Project Area (sqft) | Savings Category | Pre Consumption | Post Consumption | Bill Savings | Pre Consumption | Post Consumption | Pre - Wx Normalized | Post - Wx Normalized | Bill Savings - Wx Normalized | Electric (kWh/sqft) | Gas (therm/sqft)
1 | Library | 32000 | Cooling, pumps/fans | 352680 | 367728 | -15048 | [5 empty] | 11.0213 | 0
2 | Library | 27500 | Cooling, pumps/fans | 373056 | 248460 | 124596 | [5 empty] | 13.5657 | 0
3 | Library | 31900 | Cooling, pumps/fans | 315460 | 232320 | 83140 | [5 empty] | 9.889 | 0
4a | Library | 16345 | Cooling, pumps/fans | 76200 | 59880 | 16320 | [5 empty] | 4.662 | 0
5 | Office | 155593 | Cooling, pumps/fans | 2825280 | 2519280 | 306000 | [5 empty] | 18.1581 | 0
6 | Office | 133500 | Cooling, pumps/fans | 3138400 | 2629958 | 508442 | [5 empty] | 23.5086 | 0
7 | Office | 114421 | Cooling, pumps/fans | 1141200 | 1005120 | 136080 | [5 empty] | 9.9737 | 0
8 | Office | 118000 | Cooling, pumps/fans | 352395 | 326965 | 25430 | [5 empty] | 2.9864 | 0
9 | Office | 173000 | Cooling, pumps/fans | 835300 | 755652 | 79648 | [5 empty] | 4.8283 | 0
10 | Office | 90000 | Cooling, pumps/fans | 1933260 | 1415940 | 517320 | [5 empty] | 21.4807 | 0
11 | Office | 351063 | Cooling, pumps/fans | 4593120 | 4459680 | 133440 | [5 empty] | 13.0835 | 0
12 | Senior Center | 8250 | Cooling, pumps/fans | 38840 | 36200 | 2640 | [5 empty] | 4.7079 | 0
13 | Town Hall | 24144 | Cooling, pumps/fans | 162720 | 148320 | 14400 | [5 empty] | 6.7396 | 0
14 | Town Hall | 15600 | Cooling, pumps/fans | 93120 | 93360 | -240 | [5 empty] | 5.9692 | 0
15 | Town Hall | 14000 | Cooling, pumps/fans | 124320 | 120960 | 3360 | [5 empty] | 8.88 | 0
16 | Town Hall | 26908 | Cooling, pumps/fans | 181600 | 172320 | 9280 | [5 empty] | 6.7489 | 0
4b | Library | 16345 | Heating |  |  |  | 6211 | 5247 | 6211.3761 | 4892.721 | 1318.6551 | 0 | 0.38002
17 | Library | 14000 | Heating |  |  |  | 9558 | 7088 | 9557.8073 | 6775.5986 | 2782.2087 | 0 | 0.6827
18 | Library | 22600 | Heating |  |  |  | 15469 | 11903 | 15469.4428 | 11099.306 | 4370.1368 | 0 | 0.68449
19 | Senior Center | 14717 | Heating |  |  |  | 12594 | 9152 | 12594.3269 | 8982.7888 | 3611.5382 | 0 | 0.85577
20 | School | 128000 | Heating |  |  |  | 51181 | 49371 | 51180.9523 | 48458.1801 | 2722.7722 | 0 | 0.39985
21 | School | 57345 | Heating |  |  |  | 17736 | 21743 | 17735.7035 | 21340.9939 | -3605.2904 | 0 | 0.30928
22 | School | 68772 | Heating |  |  |  | 35672 | 37685 | 35671.9382 | 36988.2424 | -1316.3042 | 0 | 0.5187
23 | School | 50692 | Heating |  |  |  | 21524 | 18658 | 21524.053 | 18313.0324 | 3211.0206 | 0 | 0.4246
24 | Retail | 7774 | Heating |  |  |  | 4380 | 5118 | 4380.4817 | 5161.5235 | -781.0417 | 0 | 0.56348
Summary
|  |  | Electric (kWh) |  | Gas (therms)
Row Labels | Count of Project # | Sum of Project Area (sqft) | Sum of Pre Consumption | Sum of Bill Savings | Sum of Pre - Wx Normalized | Sum of Bill Savings - Wx Normalized
Heating | 9 | 380245 |  |  | 174326.0819 | 12313.6952
Cooling, pumps/fans | 16 | 1332224 | 16536951 | 1944808
Grand Total | 25 | 1712469 | 16536951 | 1944808 | 174326.0819 | 12313.6952
Results
| % Savings | Unit
Cooling, pumps/fans | 11.76% | kWh
Heating | 7.064% | Therm

## Assumptions (hidden)
The table below outlines and justifies assumptions used throughout the analysis.
Category | Type of Assumption | Assumption | Value | Units | Sequence used | Notes/Justification | Last updated
EUI | Building characteristic | Electric EUI - Cooling only | 0.8175 | kWh/sqft | DCV, CHW reset | 2018 CBECs. Average major fuel energy used for cooling (MFCLBTU/SQFT) for buildings in Northeast, 5,000-200,000 sqft. See "2018_cbecs_NE_for_2023_BMS_Calculator.xls" for analysis.
EUI | Building characteristic | Heating EUI - Poorly controlled building | 60 | kBtu/sqft | Schedule/setback | Engineering assumption - represents "high" EUI for buildings based on program experience and in line with CBECS data.
EUI | Building characteristic | Heating EUI - average for qualified buildings | 32.4744 | kBtu/sqft | HW reset | Average CBECS major fuel heating EUI (MFHTBTU/SQFT) for New England, buildings between 5,000 - 200,000 sqft. See "2018_cbecs_NE_for_2023_BMS_Calculator.xls" for analysis.
Ventilation | Building characteristic | Design Flow Rate - CV | 0.9 | CFM/sqft | Schedule/setback, OSS, DCV
Ventilation | Building characteristic | Design Flow Rate - VAV | 0.63 | CFM/sqft | Schedule/setback, SPR | Engineering assumption that the VAV will provide average of 70% reduced flow from CV
Ventilation | Building characteristic | Static pressure at AHU - CV | 2 | "wc |  | Value recommended by Cadeo after BMS tool review. See "MA CI - BMS Review Findings_02Aug2022.docx" for more information.
Ventilation | Building characteristic | Static pressure at AHU - VAV | 2 | "wc | OSS | Value recommended by Cadeo after BMS tool review. See "MA CI - BMS Review Findings_02Aug2022.docx" for more information.
Ventilation | Building characteristic | Fan BPp - CV | 0.00043569 |  | Schedule/setback, OSS
Ventilation | Building characteristic | Fan BPp - VAV | 6.5876e-05 |  | Schedule/setback, OSS, SPR
Ventilation | Building characteristic | Average VAV turndown | 40% |  | Schedule/setback
Ventilation | Building characteristic | % OA - Design | 15% |  | DCV (indirect, included in the OA flow rate) | Per ASHREA 62.1, Table 6-1 - using 15% OA for reasonable average ventilation requirement for all building types
Ventilation | Building characteristic | % OA in Heating Mode - CV | 15% |  | Schedule/setback, DCV | Maintain design % OA
Ventilation | Building characteristic | % OA in Heating Mode - VAV | 30% |  | Schedule/setback, DCV | During heating it is common practice to reduce supply air CFM by about 50% for VAV systems. Given that OA CFM must be maintained, the overall % OA will increase.
Equipment Efficiencies | Building characteristic | Fan Efficiency | 65% |  | SPR, indirectly to BPp for schedule, OSS
Equipment Efficiencies | Building characteristic | Motor Efficiency | 92% |  | Schedule/setback, OSS
Equipment Efficiencies | Building characteristic | Drive Efficiency | 96% |  | OSS
Equipment Efficiencies | Building characteristic | Motor Efficiency @ average turndown | 90% |  | Schedule/setback, SPR
Equipment Efficiencies | Building characteristic | Drive Efficiency @ average trundown | 93% |  | Schedule/setback, SPR
Equipment Efficiencies | Building characteristic | Steam Boiler Efficiency | 75% |  | OSS, HW reset, DCV | Steam boilers not listed in the baseline saturation study cited for other boiler efficieicnies. The Gas Boiler Market Characteristic study (https://ma-eeac.org/wp-content/uploads/Gas-Boiler-Market-Characterization-Study-Phase-II-Final-Report.pdf) mentions in a footnote that of the 130 steam boilers in the data they all had eff less than 80%. 75% used here until better recommendation provided by evaluation.
Equipment Efficiencies | Building characteristic | Non-Condensing Boiler Efficiency | 82% |  | OSS, HW reset, DCV, DAT Reset | Massachusetts C&I Customer On-Site Baseline Saturation Study. DNV. August 2021. (https://ma-eeac.org/wp-content/uploads/MA19C09-B-BSLNSAT_Report_final_08132021.pdf) Table 5-11. Majority of non-condensing boilers between 0.8-0.849, take mid point.
Equipment Efficiencies | Building characteristic | Condensing Boiler Efficiency | 92% |  | OSS, HW reset, DCV, DAT Reset | Massachusetts C&I Customer On-Site Baseline Saturation Study. DNV. August 2021. (https://ma-eeac.org/wp-content/uploads/MA19C09-B-BSLNSAT_Report_final_08132021.pdf) Table 5-11. Majority of condensing boilers between 0.9-0.949, take mid point.
Equipment Efficiencies | Building characteristic | Furnace Efficiency | 92% |  | Project Savings tab | Massachusetts C&I Customer On-Site Baseline Saturation Study. DNV. August 2021. (https://ma-eeac.org/wp-content/uploads/MA19C09-B-BSLNSAT_Report_final_08132021.pdf) Table 5-19. 61% of furnaces are between 91-95% AFUE.
Equipment Efficiencies | Building characteristic | Heat Pump Heating COP | 3 |  | Project Savings tab | Massachusetts C&I Customer On-Site Baseline Saturation Study. DNV. August 2021. (https://ma-eeac.org/wp-content/uploads/MA19C09-B-BSLNSAT_Report_final_08132021.pdf) Table 5-30. 49% of heat pump COPs are between 3.5-4.2, 33% are less than 3, 15% are above 4.2. COP of 3.5 used as a reasonable middle ground. However, efficiency values provided (47F performance) and MA heating season is colder. PA engineering team suggested COP 3 as better in field performance value. | 2024-02-26
Equipment Efficiencies | Building characteristic | Chiller IPLV | 0.6 | kW/ton | DAT reset, CW reset | approximately code-efficient unit. Used in ESPO custom express tools.
Temperatures | Building characteristic | Chiller Plant Design OA Temperature | 95 | deg F | DAT reset, CW reset
| Building characteristic | Chiller eff improved per degree F of DAT reset | 1% |  | DAT reset, CW reset
| Building characteristic | Chiller oversize factor | 1.2 |  | DAT reset, CW reset
Temperatures | Building characteristic | Average CV & VAV (occ/unocc) Building Balance Point, F (averaging CV and VAV balance pointsocc and unocc) | 66 | deg F | DAT reset
Temperatures | Building characteristic | Cooling Mode - OAT upper limit, degree F (at this OAT, the DAT reset is permitted; DAT is at the lower limit) | 70 | deg F | DAT reset, CW reset
Temperatures | Building characteristic | Cooling Mode - OAT lower limit, degree F (at this OAT, the DAT is at the higher limit) | 55 | deg F | DAT reset
| Building characteristic | sqft per ton Chiller sizing- based on 1 ton/ 450 square feet | 450 | ton/sqft | DAT reset, CW reset
Temperatures | Building characteristic | Cooling mode - Baseline discharge air temp | 55 | deg F | DAT reset
Temperatures | Building characteristic | Cooling mode - Discharge Air Temperature upper limit, degree F (maximum DAT allowed by customer) | 60 | deg F | DAT reset
Temperatures | Building characteristic | Minimum outdoor air temperature for chiller operation (below this temperature, there is no need for the chiller to run) | 38 | deg F | DAT reset, CW reset
| Building characteristic | Chiller Capacity | 1 | tons | DAT reset, CW reset
Temperatures | Building characteristic | Boiler Plant design OA Temperature, degree F | 0 |  | DAT reset
| Building characteristic | Boiler efficiency improved per degree F of DAT reset | 0.2% |  | DAT reset
| Building characteristic | Boiler oversize factor | 1.2 |  | DAT reset
Temperatures | Building characteristic | Heating Mode - OAT upper limit, degree F (at this OAT, the DAT reset is permitted; DAT is at the lower limit) | 65 | deg F | DAT reset
Temperatures | Building characteristic | Heating Mode - OAT lower limit, degree F (at this OAT, the DAT is at the higher limit) | 30 | deg F | DAT reset
Temperatures | Building characteristic | Heating mode - Baseline discharge air temp | 75 | deg F | DAT reset
Temperatures | Building characteristic | Heating mode - Discharge Air Temperature lower limit, degree F (minimum DAT allowed by customer) | 65 | deg F | DAT reset
Temperatures | Building characteristic | Boiler lockout outdoor air temperature (above this temperature, the boiler does not run), degree F | 60 | deg F | DAT reset
| Building characteristic | BTUh per square foot Boiler sizing | 50 | Btuh/sqft | DAT reset
| Building characteristic | Boiler Capacity / sqft, in MBH | 0.05 | MBtuh/sqft | DAT reset
Temperatures | Building characteristic | Condenser Water Temperature Approach, degree F | 7 | deg F | CW reset
Temperatures | Building characteristic | Existing Leaving Condenser Water Temperature (LCWT). | 85 | deg F | CW reset
Temperatures | Building characteristic | Return Air Temperature | 70 | deg F | Schedule/setback | Industry average for return air temperature
Temperatures | Building characteristic | Return Air Temperature - building warm up | 64 | deg F | OSS | Lower than RAT used for Schedule/setbacks since building will be colder during warm up.
Temperatures | Building characteristic | Discharge Air Temperature | 80 | deg F | OSS
Temperatures | Building characteristic | Base Heating Set point - Occupied | 70 | deg F | Schedule/setback
Temperatures | Building characteristic | Base Heating Set point - Unoccupied | 68 | deg F | Schedule/setback | Assume 2 degree setback for heating in baseline
Temperatures | Building characteristic | Balance point - CV, Occupied | 66 | deg F | Schedule/setback, DCV, DAT reset | DAT reset uses average of occ, unocc and CV/VAV
Temperatures | Building characteristic | Balance point - CV, Unoccupied | 67 | deg F | Schedule/setback, DAT reset | DAT reset uses average of occ, unocc and CV/VAV
Temperatures | Building characteristic | Balance point - VAV, Occupied | 62 | deg F | Schedule/setback, DCV, DAT reset | DAT reset uses average of occ, unocc and CV/VAV
Temperatures | Building characteristic | Balance point - VAV, Unoccupied | 68 | deg F | Schedule/setback, DAT reset | DAT reset uses average of occ, unocc and CV/VAV
Temperatures | Building characteristic | Proposed Heating Set Point - Unoccupied | 64 | deg F | Schedule/setback
Temperatures | Building characteristic | Proposed Heating Balance point - Unoccupied | 64 | deg F | Schedule/setback
Other Sequence Assumptions | Savings | Heating System Distribution Losses | 10% |  | HW Reset | Engineering judgement for typical losses.
Other Sequence Assumptions | Building characteristic | Hydronic line temp - no OA reset, non cond boiler | 180 | deg F | HW Reset
Other Sequence Assumptions | Building characteristic | Hydronic line temp - with OA reset, non cond boiler | 160 | deg F | HW Reset
Other Sequence Assumptions | Building characteristic | Hydronic line temp - no OA reset, cond boiler | 160 | deg F | HW Reset
Other Sequence Assumptions | Building characteristic | Hydronic line temp - with OA reset, cond boiler | 145 | deg F | HW Reset
Other Sequence Assumptions | Savings | # hours reduced with OSS per day | 0.7 | hour/day | OSS | Engineering judgement for typical reduction
Other Sequence Assumptions | Building characteristic | Base case fan run hours | 7300 | hours/year | Schedule/setback | Assume 4 hours unoccupied every day
Other Sequence Assumptions | Building characteristic | Heating Hours/year | 5100 | hours/year |  | Represents full heating season operation. Aligned with evaluation of steam traps. https://ma-eeac.org/wp-content/uploads/MA-CIEC-Stage-5-Final-Report-MA20C05-G-STBE-FINAL-20201020.pdf
Other Sequence Assumptions | Building characteristic | Heating weeks/year | 30.3571 | weeks/year
Other Sequence Assumptions | Building characteristic | Temp contribution - people and lighting | 3 | deg F | Schedule/setback | only during occupied hours
Other Sequence Assumptions | Building characteristic | Temp contribution - plug load | 1 | deg F | Schedule/setback | during all hours
Other Sequence Assumptions | Savings | % Time Building has Low Occupancy | 20% |  | DCV | It is conservative to assume that the building will have low occupancy 20% of the occupied building hrs time.
Other Sequence Assumptions | Savings | % of eligible cooling not locked out by economizer | 60% |  | DCV | Estimated percentage of time the return air temp comparison to the outside air temp will not enable the economizer mode/open the OA damper.
Other Sequence Assumptions | Savings | % Reduction in Cooling | 50% |  | DCV | Assumed reduction of mechanical cooling as a result of economizer over DCV
Other Sequence Assumptions | Savings | % time site qualifies for DCV | 20% |  | DCV | This worksheet assumed DCV could be implemented 20% of the time. This 20% is representative of times when DCV overrides the economizer mode in other words, the temperature or enthalpy conditions are not eligible to open the OA damper due to economizing, but the OA damper would open because the concentration of CO2 is in the space is high enough to open the outside air damper.
Other Sequence Assumptions | Building characteristic | Ave Temp Increase in Chilled Water | 5 |  | CHW reset
Other Sequence Assumptions | Savings | Reduced Compressor power/deg | 2% |  | CHW reset
Other Sequence Assumptions | Savings | % Cooling energy from compressor | 85% |  | CHW reset
Other Sequence Assumptions | Building characteristic | Cooling hours for CHW reset | 1482 |  | CHW reset
Other Sequence Assumptions | Building characteristic | Total Cooling Hours | 3470 |  | CHW reset
Other Sequence Assumptions | Savings | % Savings | 24.6% |  | SPR | Environmental Security Technology Certification Program for Dept of Defense Demonstration of Energy Savings for Commercial Buildings for Tiered Trim and Response Method of Resetting Static Pressure for VAV Systems March, 2017. https://apps.dtic.mil/sti/pdfs/AD1034401.pdf
Other Sequence Assumptions | Building characteristic | Fan run hours | 4642.2423 | hours | SPR | See TMY3 data table from Schedule tab - occupied + unoccuied fan hours
Other Sequence Assumptions | Savings | Adjustment | 70% |  | SPR | There are multiple reasons why Static Pressure Reset may not work to design. If one space is continually drawing most of the airflow, the system maynot be able to reduce airflow enough for reset to occur. If the dampers are poorly maintained and prone to stick, reset may not occur. If the BMS is a mixture of platforms and do not communicate well throughout the site, reset will be sporatic. All of these reasons occur sufficiently that an expectation of 100% at design is unrealistically optimistic. Consequently we accepted 70% of potential savings.
Savings Factor Adjustments | Conversion | kWh to Btu Conversion | 3412 | Btu/kwh | Project Savings tab
Savings Factor Adjustments | Conversion | Btu to Mbtu | 1000 | kbtu/Btu | Project Savings tab, DAT reset
Savings Factor Adjustments | Conversion | MBtu = 1 MMBtu | 1000 | Mbtu/MMBtu | DAT reset
Savings Factor Adjustments | Savings | Schedule adjustment - 5 to 7 day operation | 1.4 |  | Project Savings tab | Ratio of 5 to 7 days
Project Calculations | Conversion | MMBtu to therm | 10
Project Calculations | Conversion | Gal Oil to kbtu | 138.5 | kbtu/gal oil |  | https://www.eia.gov/energyexplained/units-and-calculators/british-thermal-units.php
Project Calculations | Conversion | Gal Propane to MMbtu | 91.452 | kbtu/gal propane |  | https://www.eia.gov/energyexplained/units-and-calculators/british-thermal-units.php
Project Calculations | Building characteristic | Base % Building Electric Savings | 11.76% |  | Project Savings tab | See "Building Savings" tab for billing analysis.
Project Calculations | Building characteristic | Base % Building Gas Savings | 7.064% |  | Project Savings tab | See "Building Savings" tab for billing analysis.
Project Calculations | Building characteristic | Additional % Savings for Ongoing Optimization | 3% |  | Project Savings tab | Program assumption. Attributes small additional savings for systems that optimize control over time through machine learning, AI, etc. Applies to Subscription Based Controls only | 2024-02-26
Project Calculations | Building characteristic | Added % savings potential for chiller | 1% |  | Project Savings tab | Program assumption
Project Calculations | Building characteristic | Default assumed % of annual fuel consumption used for base load | 28.2% |  |  | CBECS 2018, Table E7. % of Total natural gas consumption for Space Heating in New England is 72%.
Project Calculations | Building characteristic | Default % electric energy used for heating in buildings with heat pumps | 12.4% |  |  | CBECS 2018 analysis of microdata. Value developed based on buidlings in New England (Region = 1), electric system for primary heat (ELHT1 = 1). 12% is the ratio electric energy used for heating (ELHT) compared to total electric consumption (ELCN), weighted by building area. Note that the data is available for buildings that use HPs (MAINHT = 11), but the result included only 11 buildings and was not as conservative a result as the average overall. The HP result was 6%, which if used in this tool would not impact heating saving (since there are no heating savings counted for HPs), but higher cooling/fan savings (since the cooling/fan savings would apply to 94% of the building electric consumption if we assume 6% electric energy used for heating). See "2018_cbecs_NE_for_2023_BMS_Calculator.xls" for analysis.
Project Calculations | Building characteristic | Default % electric energy used for heating in buildings with electric resistance | 20.99% |  |  | CBECS 2018 analysis of microdata. Value developed based on buidlings in New England (Region = 1), electric system for primary heat (ELHT1 = 1). 21% is the ratio electric energy used for heating (ELHT) compared to total electric consumption (ELCN), weighted by building area, for electric furnaces, electric packaged units, and electric boilers (MAINHT = 1, 2, 3, respectively). The value aligns fairly well with a rule of thumb that buildings use 20% of energy for heating in the northeast. See "2018_cbecs_NE_for_2023_BMS_Calculator.xls" for analysis.
Project Calculations | Savings | Load factor converting Annual kWh to Max kW | 0.0016 |  | Project Savings and Incentive Calcs | 2025-2027 BC Model. Values from Load Shape ID ls_112 "C&I Heating & Cooling (Non-HPs). | 2025-01-01
Project Calculations | Savings | Summer Coincident % | 28% |  | Project Savings and Incentive Calcs | 2025-2027 BC Model. Values from Load Shape ID ls_112 "C&I Heating & Cooling (Non-HPs). | 2025-01-01
Project Calculations | Savings | Winter Coincident % | 7% |  | Project Savings and Incentive Calcs | 2025-2027 BC Model. Values from Load Shape ID ls_112 "C&I Heating & Cooling (Non-HPs). | 2025-01-01
Project Calculations | Savings | % Energy Savings during Summer On Peak | 35% |  |  | 2022-2024 Statewide Electric BC Model. C&I Heating & Cooling Loadshape. Summer On Peak is defined as the period between 7am - 11pm, M-F, June-Sept, excluding holidays | Do not use starting 2025
Project Calculations | Savings | % Energy Savings during Winter On Peak | 26% |  |  | 2022-2024 Statewide Electric BC Model. C&I Heating & Cooling Loadshape. Winter On Peak is defined as the period between 7am - 11pm, M-F, Oct-May, excluding holidays | Do not use starting 2025
Project Calculations | Savings | Hours in Summer On Peak Period | 1380 |  |  | 2022-2024 Statewide Electric BC Model. C&I Heating & Cooling Loadshape. Summer On Peak is defined as the period between 7am - 11pm, M-F, June-Sept, excluding holidays | Do not use starting 2025
Project Calculations | Savings | Hours in Winter On Peak Period | 2600 |  |  | 2022-2024 Statewide Electric BC Model. C&I Heating & Cooling Loadshape. Winter On Peak is defined as the period between 7am - 11pm, M-F, Oct-May, excluding holidays | Do not use starting 2025
Project Calculations | Benefits | Summer kW, Winter kW, Gas Heating, Annual kWh | varies | $/savings | Incentive Calc | Benefits are estimated based on 2025 avoided costs and the prescriptive BMS loadshape. See "Estimate_Allocation_gas_electric_benefits_2025.xlsx" for estimate of avoided costs.
Project Calculations | Measure Life | Installation of New Traditional BMS | 15 |  |  | Citation TBD - approved by EMV February 2024
Project Calculations | Measure Life | Upgrade of Traditional BMS | 5 |  |  | ERS Measure Life Study, 2005
Project Calculations | Measure Life | Subscription Based Control | 1-5 |  |  | Measure life will depend on how many years project has been pre-paid, up to 5 years

## Static Pressure Reset (hidden)
Savings Type | Theoretical Savings | Discussion
Cooling: | No
Heating: | No
Pumps/Fans: | Yes | Static Pressure Reset (SPR) calculations are based on the assumption that 7 Day Sch / Unocc Setback has been implemented. Static Pressure Reset will ONLY work on VAV systems. It is not universally applicable, if some spaces in the building have consistent high loads the dampers will not be allowed to close enough for Static Pressure Reset to work. Another way to consider the savings is CFM X ∆P /(6356 X fan eff). Static pressure upstream of the VAV box tends to be about 1.75 " to 2.5" w.c. which is fine at design flow conditions. But for most of the year supply airflow is less than design, reaching a low of 50% during the heating season. The necessary pressure upstream of the terminal box will decline by (∆ flow %)^2 . The 50% reduction in airflow results in pressure of 0.44 " w.c. (1.75" X 50%^2 = 0.44 "). The pressure can not decline too far, otherwise it will impair the ability to "throw" the conditioned air at the diffuser. Key point is the 25% reduction in fan energy from SPR seen from the DOD study seems plausible.
Formula
Static Pressure Savings | = | Annual Fan Energy Use * % Savings * Adjustment
Annual Fan Energy Use | = | VAV BHp *0.746 / (motor eff @ avg turndown * drive eff @ avg turndown) * proposed run hours
Where
Fan Savings | Term | Value | Units | Note
| Conversion HP to kW | 0.746 | kW/HP
| Fan Eff | 65% |  | Also used in OSS, scheduling
| Motor Eff @ avg turndown | 90% |  | also used for scheduling
| Drive Eff @ avg turndown | 93% |  | also used for scheduling
| % Savings | 24.6% |  | Environmental Security Technology Certification Program for Dept of Defense Demonstration of Energy Savings for Commercial Buildings for Tiered Trim and Response Method of Resetting Static Pressure for VAV Systems March, 2017. https://apps.dtic.mil/sti/pdfs/AD1034401.pdf
| Proposed Fan Run Hours | 4642.2423 | hours | See TMY3 data table from Schedule tab - occupied + unoccuied fan hours
| Adjustment | 70% |  | There are multiple reasons why Static Pressure Reset may not work to design. If one space is continually drawing most of the airflow, the system maynot be able to reduce airflow enough for reset to occur. If the dampers are poorly maintained and prone to stick, reset may not occur. If the BMS is a mixture of platforms and do not communicate well throughout the site, reset will be sporatic. All of these reasons occur sufficiently that an expectation of 100% at design is unrealistically optimistic. Consequently we accepted 70% of potential savings.
VAV | VAV - Design flow | 0.63 | CFM/ft2
| VAV BHp | 6.5876e-05
Savings
Annual Fan Energy Use | 0.27256
VAV Circ Savings | 0.046935 | kWh/sqft

## Schedule (hidden)
Savings Type | Theoretical Savings | Discussion
Cooling: | No | In New England HVAC space cooling requires about 1/10th the energy used for space heating. In addition most of the cooling load occurs when the building is occupied, so night setback has little impact.
Heating: | Yes* | Savings come from two components: envelope losses and ventilation losses. The savings only occur during unoccupied periods.
Envelope losses are calculated as UA∆T, we are not changing the insulation properties of the envelope so U is constant. We are not changing the Area so A is constant. We are changing the ∆T from 70°F to some setback value, assumed 64° F. The heat load during unoccuiped hours comes from HVAC and plug loads since people are gone, lightings are off, and the sun has set.
Ventilation should halt when the building is in Unocc mode. Its possible the legacy system doesn't recognize Unocc mode so ventilation occurs 24/7. In theory ventilation should always be a constant value to account for people and off gasing. For a VAV system if the design OA is 15% of supply, it will be 30% of supply in heat mode if supply CFM declines 50%, a common design. i.e., the office AHUs supply 50,000 CFM of which 7,500 CFM is OA. If it’s a VAV system the supply airflow will decrease to roughly 25,000 CFM when the heating season kicks in. The ventilation should remain at 7,500 CFM so the ventilation when cooling is 15% but is 30% when the HVAC system is heating. Therefore the ventilation CFM will be the same, regardless if the system is VAVor CV.
Pumps/Fans: | Yes | Scheduling can reduce fan run hours significantly.
The tool was reviewed by Cadeo in 2022 as part of an evaluation review of the TRM. Cadeo recommended using a static pressure of 2": We recommend using a lower static pressure or consider changing the calculator to adjust static pressure based on a split between buildings three stories or fewer and more than three stories. Based on our experience, 3.5” water column (WC) and 5.5” WC static pressure is very high, potentially representing a high-pressure cutout value rather than a standard operating value. We would expect the value to be closer to 2” WC. The Regional Technical Forum (RTF) assumes 1.5” WC. Two- and three-story buildings typically have low-pressure systems at less than 3” WC, while medium pressure systems, more typical for buildings taller than three stories, are more aligned with the static pressure currently cited in the tool. (Continuing Education & Development, HVAC – How to Size and Design Ducts, by A. Bhatia, Course No. M0032, accessed July 27, 2022, https://www.cedengineering.com/userfiles/HVAC%20-%20How%20to%20Size%20and%20Design%20Ducts%20R1.pdf.)
Formulas
CV Circ Savings | = | CV BHp * 0.746 / Motor Eff * (Base hours - Proposed hours)
VAV Circ Savings | = | VAV BHp * 0.746 / (0.9 * 0.95) * (Base hours - Proposed hours)
Envelope losses therms/ft2 | = | (Baseline envelope losses - Proposed envelope losses)
Ventilation losses therms/fts | = | Baseline Unoccupied ventilation energy
Total Heating therms/fts2 | = | Envelope savings + Ventilation savings
Where
On Assumptions tab
Circulation System Savings | Term | Value | Units | Note
| Conversion HP to kW | 0.746 | kW/HP
| Motor Eff | 92%
| Base case fan run hours | 7300 | hours |  |  | 0.63592
| Proposed case fan hours | 4642.2423 | hours | See TMY3 data table - occupied + unoccuied fan hours
CV | CV - Design Flow | 0.9 | CFM/ft2
| CV BPp | 0.00043569
VAV | VAV - Design flow | 0.63 | CFM/ft2
| VAV BHp | 6.5876e-05
| Motor Eff @ avg turndown | 90%
| Drive Eff @ avg turndown | 93%
Heating Savings | Term | Value | Units | Note
| Constant | 1.08
| Mbtu to Btu | 1000 | Btu/Mbtu
| RAT | 70 | deg F
| % OA heating mode - CV | 15%
| % OA heating mode - VAV | 30%
Base case | Heating EUI - poorly building | 60 | Mbtu/ft2
| Occupied set point - heating | 70 | deg F
| Unoccupied set point - heating | 68 | deg F
| CV Occupied balance point | 66 | deg F
| CV Unoccupied balance point | 67 | deg F
| VAV Occupied Balance Point | 62 | deg F
| VAV Unoccupied balance point | 68 | deg F
Proposed | Unoccupied setpoint | 64 | deg F
| Unoccupied balance point | 63 | deg F
Annual Savings
CV Fan Savings | 0.93895 | kWh/ft2
VAV Fan Savings | 0.15605 | kWh/ft2
Envelope loss savings | 4.0322 | kBtu/ft2
ventilation savings | 14.9651 | kBtu/ft2
Heating kbtu/ft2 | 18.9972 | kBtu/ft2
% envelope savings from total heating | 21.22%
| TMY 3 data Worcester |  |  | Occupancy |  |  |  | Occupied |  |  |  |  | Base Case - Unoccupied |  |  |  | Proposed - Unoccupied
Mode | Bin | average temp | hrs/yr | Occupied Hours (M-F 6AM to 6PM hrs/yr) | Unocc hrs | Unocc fan run hrs | % time fans run during unocc | Occupied (∆T * Occ hours) | CV - Occupied Mixed Chamber Air Temp | CV - Occupied Ventilation MBTUs | VAV - Occupied Mixed Chamber Air Temp | VAV - Occupied Ventilation MBTUs | Unoccupied (∆T * Unocc hours) | Total (∆T * Unocc hours) | CV - Unoccupied Ventilation MBTUs | VAV - Unoccupied Ventilation MBTUs | Unoccupied (∆T * Unocc hours) | Total (∆T * Unocc hours)
Cooling | 95 to 99 | 97 | 0 | 0 | 0 | 0 | 25%
Cooling | 90 to 94 | 92 | 0 | 0 | 0 | 0 | 25%
Cooling | 85 to 89 | 87 | 25 | 20 | 5 | 1.25 | 25%
Cooling | 80 to 84 | 82 | 125 | 91 | 34 | 6.8 | 20%
Cooling | 75 to 79 | 77 | 336 | 236 | 100 | 0 | 0%
Cooling | 70 to 74 | 72 | 423 | 239 | 184 | 0 | 0% |  |  |  | 70.6
Cooling | 65 to 69 | 67 | 718 | 309 | 409 | 0 | 0% | 0 |  |  | 69.1 | 0 | 0 | 0 |  |  | 0 | 0
Cooling | 60 to 64 | 62 | 1050 | 328 | 722 | 0 | 0% | 1312 | 68.8 |  | 67.6 | 0 | 3610 | 4922 | 0 | 0.1965 | 722 | 2034
Cooling | 55 to 59 | 57 | 793 | 259 | 534 | 53.4 | 10% | 2331 | 68.05 | 0 | 66.1 | 0 | 5340 | 7671 | 0 | 0.69033 | 3204 | 5535
Heating | 50 to 54 | 52 | 646 | 236 | 410 | 63.0769 | 15.38% | 3304 | 67.3 | 0 | 64.6 | 0 | 6150 | 9454 | 0 | 0.94848 | 4510 | 7814
Heating | 45 to 49 | 47 | 459 | 182 | 277 | 57.5308 | 20.77% | 3458 | 66.55 | 0 | 63.1 | 0 | 5540 | 8998 | 0.12116 | 0.92351 | 4432 | 7890
Heating | 40 to 44 | 42 | 648 | 212 | 436 | 114.0308 | 26.15% | 5088 | 65.8 | 0.041213 | 61.6 | 0.057698 | 10900 | 15988 | 0.50855 | 1.8986 | 9156 | 14244
Heating | 35 to 39 | 37 | 857 | 275 | 582 | 183.5538 | 31.54% | 7975 | 65.05 | 0.25394 | 60.1 | 0.35551 | 17460 | 25435 | 1.1031 | 3.1283 | 15132 | 23107
Heating | 30 to 34 | 32 | 787 | 287 | 500 | 184.6154 | 36.92% | 9758 | 64.3 | 0.47424 | 58.6 | 0.66393 | 17500 | 27258 | 1.3122 | 3.1979 | 15500 | 25258
Heating | 25 to 29 | 27 | 564 | 198 | 366 | 154.8462 | 42.31% | 7722 | 63.55 | 0.47152 | 57.1 | 0.66012 | 14640 | 22362 | 1.2273 | 2.7144 | 13176 | 20898
Heating | 20 to 24 | 22 | 527 | 176 | 351 | 167.4 | 47.69% | 7744 | 62.8 | 0.54743 | 55.6 | 0.7664 | 15795 | 23539 | 1.4329 | 2.9614 | 14391 | 22135
Heating | 15 to 19 | 17 | 330 | 152 | 178 | 94.4769 | 53.08% | 7448 | 62.05 | 0.58359 | 54.1 | 0.81702 | 8900 | 16348 | 0.85643 | 1.6834 | 8188 | 15636
Heating | 10 to 14 | 12 | 263 | 88 | 175 | 102.3077 | 58.46% | 4752 | 61.3 | 0.40202 | 52.6 | 0.56283 | 9625 | 14377 | 0.96957 | 1.8337 | 8925 | 13677
Heating | 5 to 9 | 7 | 126 | 59 | 67 | 42.7769 | 63.85% | 3481 | 60.55 | 0.31255 | 51.1 | 0.43757 | 4020 | 7501 | 0.42005 | 0.77042 | 3752 | 7233
Heating | 0 to 4 | 2 | 55 | 25 | 30 | 20.7692 | 69.23% | 1600 | 59.8 | 0.15066 | 49.6 | 0.21092 | 1950 | 3550 | 0.20995 | 0.37558 | 1830 | 3430
Heating | -1 to -5 | -3 | 16 | 5 | 11 | 8.2077 | 74.62% | 345 | 59.05 | 0.033777 | 48.1 | 0.047288 | 770 | 1115 | 0.085001 | 0.14894 | 726 | 1071
Heating | -6 to -10 | -8 | 9 | 3 | 6 | 4.8 | 80% | 222 | 58.3 | 0.022453 | 46.6 | 0.031434 | 450 | 672 | 0.050738 | 0.087363 | 426 | 648
Heating | -11 to -15 | -13 | 3 | 0 | 3 | 2.4 | 80% | 0 | 57.55 | 0 | 45.1 | 0 | 240 | 240 | 0.027556 | 0.046743 | 228 | 228
| totals |  | 8760 | 3380 | 5380 | 1262.2423 |  | 66540 | 1010.8 | 3.2934 | 1041.3 | 4.6107 | 122890 | 189430 | 8.3246 | 21.6056 | 104298 | 170838
4089
|  |  | 46.68% | [12 empty] | Reduction in envelope losses | 9.815%
[16 empty] | Occ - energy loss for ventilation | 3.9521 | kBtu/ft2
[16 empty] | Unocc - energy loss for ventilation | 14.9651 | kBtu/ft2
[16 empty] | Total ventilation losses | 18.9171 | kBtu/ft2
[16 empty] | Base case - envelope losses | 41.0829 | kBtu/ft2
[16 empty] | Proposed case - envelope losses | 37.0507 | kBtu/ft2
Note on I56: Brougher, Whitney: occupied internal loads include people, lighting, plug loads
Note on N56: Brougher, Whitney: unoccupied internal loads - plug loads only (no people or lights)
Note on R56: Brougher, Whitney: unoccupied internal loads - plug loads only (no people or lights)
Note on S56: Brougher, Whitney: Occupied same as basecase

## Opt StartStop (hidden)
Savings Type | Theoretical Savings | Discussion
Cooling: | No
Heating: | Yes* | Optimal Start/Stop is a programming strategy to minimize morning warmup, in essence it expands the unoccupied period by about 2% . When in morning warmup the heating system is in full fire mode to bring the building mass back to occupied temperatures. Most of the unoccupied period the heating system is in low to mid fire, a reduction in morning warmup is therefore magnified compared to typical unoccupied heating.
Pumps/Fans: | Yes | In heat mode a VAV system may have supply airflow roughly 50% of design, while a constant volume system remains at design airflow. However for morning warmup the OA dampers should close, and the fan will run at design CFM to recover the building mass back to occupied setpoint temps. Consequently both CV and VAV will run at the same CFM. VAV systems will have longer duct runs and terminal boxes to reach the final heat emitters, the pressure drop will be greater so the VAV power should be greater than for CV.
Formulas:
Heating savings | = | CV Design Flow * 1.08 * (Discharge Temp - RA Temp) * (Reduction in Run Time) /(1000 * Boiler Eff)
CV Circulation savings | = | CV BHp * 0.747 / (Motor Eff*Drive Eff) * Reduction in Run Time
VAV Circulation savings | = | VAV BHp * 0.747 / (Motor Eff*Drive Eff) * Reduction in Run Time
Where:
Savings Type | Term | Value | Units | Note
Heating | CV Design Flow | 0.9 | CFM/sqft
| Constant | 1.08
| Discharge Temp | 80 | deg F
| Return Air Temp - building warm up | 64 | deg F
| # hour reduction per day | 0.7
| Reduction in Run Time | 106.25 | hours/year | Assumes 0.7 hr reduction per day, 5 days/week, 30 heating weeks/year
| Btu to kbtu conversion | 1000 | kbtu/Btu
| Non-condensing Boiler eff | 82%
| Condensing Boiler Eff | 92%
Circulation | Motor Eff | 92%
| Drive Eff | 96%
| Fan Eff | 65%
| Static pressure at AHU - VAV | 2 | "wc
| CV BHp | 0.00043569
| VAV BHp for building warm up | 0.00043569 |  | Use CV Design flow since dampers are closed and run at full design CFM to bring building to temp.
Savings
Heating - Non-Condensing | 2.0151 | kbtu/ft2
Heating - Condensing | 1.7961 | kbtu/ft2 | Note - theoretical savings were developed for Condensing Boilers, but ultimately is not used directly in the Savings Factors tables.
CV Circ Savings | 0.039153 | kWh/ft2
VAV Circ Savings | 0.039153 | kWh/ft3

## CW Reset (hidden)
Savings Type | Theoretical Savings | Discussion
Cooling: | Yes | The analysis here is taken from the ESPO Low Cost Tuning Measure Custom Express Tool for the same measure. This strategy is only applicable to water-cooled chillers. The condenser water setpoint or the temperature of the water leaving the cooling tower can be controlled based on building loads, outdoor air wet-bulb temperature, or another appropriate control variable. Assumes 10F range (temp drop from condenser water entering and leaving the cooling tower) Assumes cooling tower fan energy penalty is included in energy savings factor Chiller plant does not run during winter peak period
Heating: | No
Pumps/Fans: | No
Formula
Cooling Savings | = | Chiller kWh Saved at above design conditions/450 sq ft
Where
Cooling | Chiller Capacity, in tons used in savings calculation below | 1 | tons
| Chiller Plant Design OA Temp, degree F | 95 | deg F
| Condenser Water Temperature Approach, degree F | 7 | deg F
| Chiller IPLV (kW/ton) - approximately code-efficient unit | 0.6 | kW/ton
| Chiller energy saved per degree F of CWT reset (assume equal to chiller energy assumption per TRACE 700) | 1%
| Chiller oversize factor | 120%
| Outdoor wetbulb temp reset upper limit, F (at this temp, reset is permitted) | 70 | deg F
| Outdoor wetbulb temp reset lower limit, F (at this temp, water reset has reached minimum temperature) | 60 | deg F
| sqft per ton Chiller sizing- based on 1 ton/ 450 square feet | 450 | ton/sqft
| Condenser water temperature reset lower limit, degree F | 65 | deg F | (minimum condenser water temperature allowed by chiller manufacturer)
| Chiller lockout outdoor air temperature | 38 | deg F | (below this temperature, the chiller does not run), degree F
| Existing Leaving Condenser Water Temperature (LCWT). | 85 | deg F | assumes (Design WBT + 7F)
Savings
Cooling | 0.10222 | kWh/ft2
TMY3 Station ID to Use
725095
TYM3 Station Name
Worcester Regional Arpt
Condenser Water Reset Strategy
OAT-DB Bin (°F) | Avg WBT | Annual Bin Hours | On-Peak Bin Hours | Winter Peak Hours | Summer Peak Hours | Chiller load % | Cooling FLH | On-Peak Cooling FLH | Chiller Tons | Eff CW temp % of reset | Base CW leaving temp | Eff CW temp | % Improvement in chiller efficiency | Base Chiller kW | Eff Chiller kW | Chiller kW saved | Chiller kWh saved | On-Peak kWh saved
100 | 76 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 1 | 0% | 85 | 83 | 2% | 1 | 0 | 0 | 0 | 0
99 | 75 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 1 | 0% | 85 | 82 | 3% | 1 | 0 | 0 | 0 | 0
98 | 75 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 1 | 0% | 85 | 82 | 3% | 1 | 0 | 0 | 0 | 0
97 | 74 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 1 | 0% | 85 | 81 | 4% | 1 | 0 | 0 | 0 | 0
96 | 73 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 1 | 0% | 85 | 80 | 5% | 1 | 0 | 0 | 0 | 0
95 | 73 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 1 | 0% | 85 | 80 | 5% | 1 | 0 | 0 | 0 | 0
94 | 74 | 0 | 0 | 0 | 0 | 98% | 0 | 0 | 1 | 0% | 85 | 81 | 4% | 0 | 0 | 0 | 0 | 0
93 | 73 | 0 | 0 | 0 | 0 | 96% | 0 | 0 | 1 | 0% | 85 | 80 | 5% | 0 | 0 | 0 | 0 | 0
92 | 71 | 0 | 0 | 0 | 0 | 95% | 0 | 0 | 1 | 0% | 85 | 78 | 7% | 0 | 0 | 0 | 0 | 0
91 | 72 | 0 | 0 | 0 | 0 | 93% | 0 | 0 | 1 | 0% | 85 | 79 | 6% | 0 | 0 | 0 | 0 | 0
90 | 70 | 0 | 0 | 0 | 0 | 91% | 0 | 0 | 1 | 5% | 85 | 77 | 8% | 0 | 0 | 0 | 0 | 0
89 | 71 | 6 | 5 | 0 | 3 | 89% | 2 | 2 | 1 | 0% | 85 | 78 | 7% | 0 | 0 | 0 | 0 | 0
88 | 71 | 0 | 0 | 0 | 0 | 88% | 0 | 0 | 1 | 0% | 85 | 78 | 7% | 0 | 0 | 0 | 0 | 0
87 | 68 | 9 | 8 | 0 | 5 | 86% | 3 | 3 | 1 | 20% | 85 | 75 | 10% | 0 | 0 | 0 | 0 | 0
86 | 70 | 10 | 0 | 0 | 6 | 84% | 3 | 0 | 1 | 0% | 85 | 77 | 8% | 0 | 0 | 0 | 0 | 0
85 | 69 | 0 | 8 | 0 | 0 | 82% | 0 | 0 | 1 | 12% | 85 | 76 | 9% | 0 | 0 | 0 | 0 | 0
84 | 69 | 29 | 25 | 0 | 7 | 81% | 9 | 8 | 1 | 13% | 85 | 76 | 9% | 0 | 0 | 0 | 1 | 0
83 | 69 | 0 | 0 | 0 | 0 | 79% | 0 | 0 | 1 | 14% | 85 | 76 | 9% | 0 | 0 | 0 | 0 | 0
82 | 69 | 49 | 32 | 0 | 23 | 77% | 15 | 10 | 1 | 10% | 85 | 76 | 9% | 0 | 0 | 0 | 1 | 1
81 | 68 | 0 | 0 | 0 | 0 | 75% | 0 | 0 | 1 | 18% | 85 | 75 | 10% | 0 | 0 | 0 | 0 | 0
80 | 69 | 47 | 28 | 0 | 20 | 74% | 13 | 8 | 1 | 10% | 85 | 76 | 9% | 0 | 0 | 0 | 1 | 0
79 | 68 | 0 | 0 | 0 | 0 | 72% | 0 | 0 | 1 | 22% | 85 | 75 | 10% | 0 | 0 | 0 | 0 | 0
78 | 67 | 84 | 52 | 0 | 31 | 70% | 23 | 14 | 1 | 34% | 85 | 74 | 11% | 0 | 0 | 0 | 2 | 1
77 | 67 | 86 | 2 | 0 | 33 | 68% | 23 | 1 | 1 | 34% | 85 | 74 | 11% | 0 | 0 | 0 | 1 | 0
76 | 66 | 0 | 62 | 0 | 0 | 67% | 0 | 0 | 1 | 36% | 85 | 73 | 12% | 0 | 0 | 0 | 0 | 0
75 | 66 | 166 | 125 | 0 | 50 | 65% | 42 | 31 | 1 | 38% | 85 | 73 | 12% | 0 | 0 | 0 | 3 | 2
74 | 66 | 1 | 0 | 0 | 0 | 63% | 0 | 0 | 1 | 40% | 85 | 73 | 12% | 0 | 0 | 0 | 0 | 0
73 | 65 | 197 | 131 | 0 | 43 | 61% | 47 | 31 | 1 | 46% | 85 | 72 | 13% | 0 | 0 | 0 | 3 | 2
72 | 64 | 4 | 2 | 0 | 0 | 60% | 1 | 0 | 0 | 55% | 85 | 71 | 14% | 0 | 0 | 0 | 0 | 0
71 | 65 | 216 | 135 | 0 | 24 | 58% | 48 | 30 | 0 | 54% | 85 | 72 | 13% | 0 | 0 | 0 | 3 | 2
70 | 62 | 5 | 4 | 0 | 0 | 56% | 1 | 1 | 0 | 76% | 85 | 69 | 16% | 0 | 0 | 0 | 0 | 0
69 | 62 | 255 | 152 | 0 | 35 | 54% | 54 | 32 | 0 | 84% | 85 | 69 | 16% | 0 | 0 | 0 | 4 | 2
68 | 61 | 153 | 3 | 0 | 22 | 53% | 31 | 1 | 0 | 91% | 85 | 68 | 17% | 0 | 0 | 0 | 2 | 0
67 | 61 | 8 | 79 | 0 | 0 | 51% | 2 | 16 | 0 | 92% | 85 | 68 | 17% | 0 | 0 | 0 | 0 | 1
66 | 60 | 293 | 160 | 0 | 24 | 49% | 56 | 30 | 0 | 100% | 85 | 67 | 18% | 0 | 0 | 0 | 4 | 2
65 | 59 | 9 | 8 | 0 | 0 | 47% | 2 | 1 | 0 | 100% | 85 | 66 | 19% | 0 | 0 | 0 | 0 | 0
64 | 58 | 312 | 148 | 0 | 15 | 46% | 55 | 26 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 4 | 2
63 | 58 | 18 | 12 | 0 | 0 | 44% | 3 | 2 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
62 | 57 | 344 | 142 | 0 | 9 | 42% | 56 | 23 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 4 | 2
61 | 56 | 23 | 11 | 0 | 0 | 40% | 4 | 2 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
60 | 55 | 353 | 138 | 0 | 6 | 39% | 53 | 21 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 3 | 1
59 | 54 | 158 | 4 | 0 | 3 | 37% | 23 | 1 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 1 | 0
58 | 52 | 21 | 65 | 0 | 0 | 35% | 3 | 9 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 1
57 | 51 | 310 | 103 | 0 | 1 | 33% | 40 | 13 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 2 | 1
56 | 51 | 25 | 11 | 0 | 0 | 32% | 3 | 1 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
55 | 51 | 279 | 92 | 2 | 3 | 30% | 32 | 11 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 2 | 1
54 | 49 | 14 | 6 | 0 | 0 | 28% | 2 | 1 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
53 | 48 | 247 | 116 | 0 | 1 | 26% | 25 | 12 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 1 | 1
52 | 47 | 11 | 3 | 0 | 0 | 25% | 1 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
51 | 46 | 257 | 103 | 1 | 4 | 23% | 23 | 9 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 1 | 0
50 | 46 | 117 | 2 | 1 | 0 | 21% | 10 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
49 | 44 | 17 | 38 | 0 | 0 | 19% | 1 | 3 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
48 | 43 | 212 | 84 | 0 | 0 | 18% | 14 | 6 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
47 | 42 | 12 | 1 | 1 | 0 | 16% | 1 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
46 | 41 | 215 | 97 | 1 | 0 | 14% | 12 | 5 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
45 | 41 | 3 | 3 | 0 | 0 | 12% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
44 | 39 | 246 | 116 | 0 | 0 | 11% | 10 | 5 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
43 | 38 | 5 | 2 | 0 | 0 | 9% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
42 | 37 | 251 | 116 | 0 | 0 | 7% | 7 | 3 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
41 | 36 | 138 | 1 | 1 | 0 | 5% | 3 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
40 | 35 | 8 | 56 | 0 | 0 | 4% | 0 | 1 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
39 | 35 | 245 | 97 | 3 | 0 | 2% | 2 | 1 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
38 | 34 | 16 | 6 | 1 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
37 | 33 | 278 | 138 | 5 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
36 | 32 | 34 | 17 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
35 | 31 | 284 | 115 | 7 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
34 | 30 | 30 | 20 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
33 | 29 | 275 | 122 | 3 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
32 | 28 | 168 | 18 | 6 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
31 | 27 | 45 | 74 | 3 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
30 | 26 | 269 | 84 | 10 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
29 | 25 | 36 | 12 | 2 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
28 | 24 | 223 | 69 | 6 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
27 | 23 | 37 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
26 | 22 | 226 | 84 | 6 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
25 | 21 | 42 | 20 | 3 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
24 | 20 | 204 | 77 | 10 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
23 | 19 | 112 | 22 | 6 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
22 | 18 | 37 | 43 | 3 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
21 | 17 | 155 | 57 | 4 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
20 | 16 | 19 | 9 | 1 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
19 | 16 | 95 | 54 | 4 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
18 | 15 | 19 | 12 | 2 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
17 | 14 | 94 | 57 | 8 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
16 | 13 | 20 | 10 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
15 | 12 | 102 | 45 | 5 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
14 | 11 | 50 | 8 | 1 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
13 | 10 | 35 | 33 | 1 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
12 | 9 | 83 | 37 | 3 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
11 | 8 | 22 | 7 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
10 | 7 | 73 | 40 | 5 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
9 | 6 | 15 | 8 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
8 | 5 | 41 | 22 | 3 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
7 | 4 | 10 | 6 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
6 | 4 | 40 | 17 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
5 | 3 | 20 | 4 | 1 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
4 | 2 | 6 | 7 | 1 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
3 | 0 | 23 | 8 | 2 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
2 | 0 | 11 | 3 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
1 | -1 | 13 | 7 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
0 | -2 | 2 | 1 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
-1 | -3 | 7 | 4 | 1 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
-2 | -4 | 2 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
-3 | -5 | 5 | 2 | 1 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
-4 | -6 | 2 | 1 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
-5 | -6 | 0 | 1 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
-6 | -6 | 2 | 2 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
-7 | -6 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
-8 | -6 | 2 | 1 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
-9 | -6 | 2 | 1 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
-10 | -6 | 3 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
-11 | -6 | 2 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
-12 | -6 | 1 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
-13 | -6 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
-14 | -6 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
-15 | -6 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
-16 | -6 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
-17 | -6 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
-18 | -6 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
-19 | -6 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
-20 | -6 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
-21 | -6 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
-22 | -6 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 100% | 85 | 65 | 20% | 0 | 0 | 0 | 0 | 0
Total |  | 8760 | 3984 | 124 | 368 |  | 755 | 372 | [8 empty] | 46 | 23

## DAT reset (hidden)
Savings Type | Theoretical Savings | Discussion
Cooling: | Yes | The analysis here is taken from the ESPO Low Cost Tuning Measure Custom Express Tool for the same measure. Resets are a trade off between fan energy change vs thermal energy change. Assumes Chiller plant does not run during winter peak period (no winter kW claimed) Assumes distribution fan energy penalty is included in the energy savings factors
Heating: | Yes
Pumps/Fans: | No
Formula
Cooling Savings | = | Chiller kWh Saved at above design conditions/450 sq ft
Boiler MBH/sqft | = | 50Btuh/sqft / 1,000 Btuh/MBH
Heating Savings | = | Heating MMBtu Savings at above design conditions * 1,000 MBtu /1 MMBtu
Where
Cooling | Chiller Plant Design OA Temperature, degree F | 95
| Chiller IPLV (kW/ton) - approximately code-efficient unit | 0.6 | kW/Ton |  | on assumptions tab
| Chiller eff improved per degree F of DAT reset | 1%
| Chiller oversize factor | 120%
| Average CV & VAV (occ/unocc) Building Balance Point, F (averaging CV and VAV balance pointsocc and unocc) | 66 | deg F
| Cooling Mode - OAT upper limit, degree F (at this OAT, the DAT reset is permitted; DAT is at the lower limit) | 70 | deg F
| Cooling Mode - OAT lower limit, degree F (at this OAT, the DAT is at the higher limit) | 55 | deg F
| sqft per ton Chiller sizing- based on 1 ton/ 450 square feet | 450 | ton/sqft
| Cooling mode - Baseline discharge air temp | 55 | deg F
| Cooling mode - Discharge Air Temperature upper limit, degree F (maximum DAT allowed by customer) | 60 | deg F
| Minimum outdoor air temperature for chiller operation (below this temperature, there is no need for the chiller to run) | 38 | deg F
| Chiller Capacity, in tons used in savings calculation below | 1 | tons
Heating | Boiler Plant design OA Temperature, degree F | 0
| Non-condensing Boiler Efficiency | 82%
| Condensing Boiler Efficiency | 92%
| Boiler efficiency improved per degree F of DAT reset | 0.2%
| Boiler oversize factor | 120%
| Heating Mode - OAT upper limit, degree F (at this OAT, the DAT reset is permitted; DAT is at the lower limit) | 65 | deg F
| Heating Mode - OAT lower limit, degree F (at this OAT, the DAT is at the higher limit) | 30 | deg F
| Heating mode - Baseline discharge air temp | 75 | deg F
| Heating mode - Discharge Air Temperature lower limit, degree F (minimum DAT allowed by customer) | 65 | deg F
| Boiler lockout outdoor air temperature (above this temperature, the boiler does not run), degree F | 60 | deg F
| BTUh per square foot Boiler sizing | 50 | Btuh/sqft
| BTUh = 1MBH | 1000
| MBtu = 1 MMBtu | 1000
| Boiler Capacity / sqft, in MBH | 0.05 | MBtuh/sqft
Savings
Cooling | 0.00039762 | kWh/ft2
Heating - Non-Cond | 0.296 | Mbtu/ft2
Heating - Cond | 0.263 | Mbtu/ft2 | Note - theoretical savings were developed for Condensing Boilers, but ultimately is not used directly in the Savings Factors tables.
TMY3 Station ID to Use
725095
TYM3 Station Name
Worcester Regional Arpt
*Uses LCTM calcuator for DAT reset with above assumptions
[7 empty] | Discharge Air Temp Reset Strategy - Cooling Mode | [12 empty] | Discharge Air Temp Reset Strategy - Heating Mode
OAT-DB Bin (°F) | Avg WBT | Annual Bin Hours | On-Peak Bin Hours | Winter Peak Hours | Summer Peak Hours | HVAC Mode | Chiller load % | Cooling FLH | On-Peak Cooling FLH | Chiller Tons | Cooling Mode DAT Reset | Cooling Mode Base DAT | Cooling Mode Eff DAT | % increase in chiller efficiency | Base Chiller kW | Eff Chiller kW | Chiller kW saved | Chiller kWh saved | On-Peak chiller kWh saved | Heating Load, % | Heating FLH | Heating MBH | Heating Mode DAT Reset | Heating Mode Base DAT | Heating Mode Eff DAT | % Increase in Boiler efficiency | Base Heater kbtu/h fuel | Eff Heater kbtu/h fuel | Non- condensing MMBtu Fuel Saved | Condensing MMBtu Fuel Saved
100 | 76 | 0 | 0 | 0 | 0 | cooling mode | 100% | 0 | 0 | 1 | 0% | 55 | 55 | 0% | 1 | 1 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
99 | 75 | 0 | 0 | 0 | 0 | cooling mode | 100% | 0 | 0 | 1 | 0% | 55 | 55 | 0% | 1 | 1 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
98 | 75 | 0 | 0 | 0 | 0 | cooling mode | 100% | 0 | 0 | 1 | 0% | 55 | 55 | 0% | 1 | 1 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
97 | 74 | 0 | 0 | 0 | 0 | cooling mode | 100% | 0 | 0 | 1 | 0% | 55 | 55 | 0% | 1 | 1 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
96 | 73 | 0 | 0 | 0 | 0 | cooling mode | 100% | 0 | 0 | 1 | 0% | 55 | 55 | 0% | 1 | 1 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
95 | 73 | 0 | 0 | 0 | 0 | cooling mode | 100% | 0 | 0 | 1 | 0% | 55 | 55 | 0% | 1 | 1 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
94 | 74 | 0 | 0 | 0 | 0 | cooling mode | 98% | 0 | 0 | 1 | 0% | 55 | 55 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
93 | 73 | 0 | 0 | 0 | 0 | cooling mode | 96% | 0 | 0 | 1 | 0% | 55 | 55 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
92 | 71 | 0 | 0 | 0 | 0 | cooling mode | 95% | 0 | 0 | 1 | 0% | 55 | 55 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
91 | 72 | 0 | 0 | 0 | 0 | cooling mode | 93% | 0 | 0 | 1 | 0% | 55 | 55 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
90 | 70 | 0 | 0 | 0 | 0 | cooling mode | 91% | 0 | 0 | 1 | 0% | 55 | 55 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
89 | 71 | 6 | 5 | 0 | 3 | cooling mode | 89% | 2 | 2 | 1 | 0% | 55 | 55 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
88 | 71 | 0 | 0 | 0 | 0 | cooling mode | 88% | 0 | 0 | 1 | 0% | 55 | 55 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
87 | 68 | 9 | 8 | 0 | 5 | cooling mode | 86% | 3 | 3 | 1 | 0% | 55 | 55 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
86 | 70 | 10 | 0 | 0 | 6 | cooling mode | 84% | 3 | 0 | 1 | 0% | 55 | 55 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
85 | 69 | 0 | 8 | 0 | 0 | cooling mode | 82% | 0 | 0 | 1 | 0% | 55 | 55 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
84 | 69 | 29 | 25 | 0 | 7 | cooling mode | 81% | 9 | 8 | 1 | 0% | 55 | 55 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
83 | 69 | 0 | 0 | 0 | 0 | cooling mode | 79% | 0 | 0 | 1 | 0% | 55 | 55 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
82 | 69 | 49 | 32 | 0 | 23 | cooling mode | 77% | 15 | 10 | 1 | 0% | 55 | 55 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
81 | 68 | 0 | 0 | 0 | 0 | cooling mode | 75% | 0 | 0 | 1 | 0% | 55 | 55 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
80 | 69 | 47 | 28 | 0 | 20 | cooling mode | 74% | 13 | 8 | 1 | 0% | 55 | 55 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
79 | 68 | 0 | 0 | 0 | 0 | cooling mode | 72% | 0 | 0 | 1 | 0% | 55 | 55 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
78 | 67 | 84 | 52 | 0 | 31 | cooling mode | 70% | 23 | 14 | 1 | 0% | 55 | 55 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
77 | 67 | 86 | 2 | 0 | 33 | cooling mode | 68% | 23 | 1 | 1 | 0% | 55 | 55 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
76 | 66 | 0 | 62 | 0 | 0 | cooling mode | 67% | 0 | 0 | 1 | 0% | 55 | 55 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
75 | 66 | 166 | 125 | 0 | 50 | cooling mode | 65% | 42 | 31 | 1 | 0% | 55 | 55 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
74 | 66 | 1 | 0 | 0 | 0 | cooling mode | 63% | 0 | 0 | 1 | 0% | 55 | 55 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
73 | 65 | 197 | 131 | 0 | 43 | cooling mode | 61% | 47 | 31 | 1 | 0% | 55 | 55 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
72 | 64 | 4 | 2 | 0 | 0 | cooling mode | 60% | 1 | 0 | 0 | 0% | 55 | 55 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
71 | 65 | 216 | 135 | 0 | 24 | cooling mode | 58% | 48 | 30 | 0 | 0% | 55 | 55 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
70 | 62 | 5 | 4 | 0 | 0 | cooling mode | 56% | 1 | 1 | 0 | 0% | 55 | 55 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
69 | 62 | 255 | 152 | 0 | 35 | cooling mode | 54% | 54 | 32 | 0 | 7% | 55 | 55 | 0% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
68 | 61 | 153 | 3 | 0 | 22 | cooling mode | 53% | 31 | 1 | 0 | 13% | 55 | 56 | 1% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
67 | 61 | 8 | 79 | 0 | 0 | cooling mode | 51% | 2 | 16 | 0 | 20% | 55 | 56 | 1% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
66 | 60 | 293 | 160 | 0 | 24 |  | 49% | 56 | 30 | 0 | 27% | 55 | 56 | 1% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
65 | 59 | 9 | 8 | 0 | 0 | heating mode | 47% | 2 | 1 | 0 | 33% | 55 | 57 | 2% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 100% | 75 | 65 | 2% | 0 | 0 | 0 | 0
64 | 58 | 312 | 148 | 0 | 15 | heating mode | 46% | 55 | 26 | 0 | 40% | 55 | 57 | 2% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 97% | 75 | 65 | 1.943% | 0 | 0 | 0 | 0
63 | 58 | 18 | 12 | 0 | 0 | heating mode | 44% | 3 | 2 | 0 | 47% | 55 | 57 | 2% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 94% | 75 | 66 | 1.886% | 0 | 0 | 0 | 0
62 | 57 | 344 | 142 | 0 | 9 | heating mode | 42% | 56 | 23 | 0 | 53% | 55 | 58 | 3% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 91% | 75 | 66 | 1.829% | 0 | 0 | 0 | 0
61 | 56 | 23 | 11 | 0 | 0 | heating mode | 40% | 4 | 2 | 0 | 60% | 55 | 58 | 3% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 89% | 75 | 66 | 1.771% | 0 | 0 | 0 | 0
60 | 55 | 353 | 138 | 0 | 6 | heating mode | 39% | 53 | 21 | 0 | 67% | 55 | 58 | 3% | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 86% | 75 | 66 | 1.714% | 0 | 0 | 0 | 0
59 | 54 | 158 | 4 | 0 | 3 | heating mode | 37% | 23 | 1 | 0 | 73% | 55 | 59 | 4% | 0 | 0 | 0 | 0 | 0 | 2% | 1 | 0 | 83% | 75 | 67 | 1.657% | 0 | 0 | 2e-06 | 2e-06
58 | 52 | 21 | 65 | 0 | 0 | heating mode | 35% | 3 | 9 | 0 | 80% | 55 | 59 | 4% | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 80% | 75 | 67 | 1.6% | 0 | 0 | 1e-06 | 1e-06
57 | 51 | 310 | 103 | 0 | 1 | heating mode | 33% | 40 | 13 | 0 | 87% | 55 | 59 | 4% | 0 | 0 | 0 | 0 | 0 | 5% | 9 | 0 | 77% | 75 | 67 | 1.543% | 0 | 0 | 1.2e-05 | 1.1e-05
56 | 51 | 25 | 11 | 0 | 0 | heating mode | 32% | 3 | 1 | 0 | 93% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 7% | 1 | 0 | 74% | 75 | 68 | 1.486% | 0 | 0 | 1e-06 | 1e-06
55 | 51 | 279 | 92 | 2 | 3 | heating mode | 30% | 32 | 11 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 8% | 13 | 0 | 71% | 75 | 68 | 1.429% | 0 | 0 | 1.7e-05 | 1.5e-05
54 | 49 | 14 | 6 | 0 | 0 | heating mode | 28% | 2 | 1 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 10% | 1 | 0 | 69% | 75 | 68 | 1.371% | 0 | 0 | 1e-06 | 1e-06
53 | 48 | 247 | 116 | 0 | 1 | heating mode | 26% | 25 | 12 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 12% | 16 | 0 | 66% | 75 | 68 | 1.314% | 0 | 0 | 2e-05 | 1.8e-05
52 | 47 | 11 | 3 | 0 | 0 | heating mode | 25% | 1 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 13% | 1 | 0 | 63% | 75 | 69 | 1.257% | 0 | 0 | 1e-06 | 1e-06
51 | 46 | 257 | 103 | 1 | 4 | heating mode | 23% | 23 | 9 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 15% | 21 | 0 | 60% | 75 | 69 | 1.2% | 0 | 0 | 2.4e-05 | 2.1e-05
50 | 46 | 117 | 2 | 1 | 0 | heating mode | 21% | 10 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 17% | 11 | 0 | 57% | 75 | 69 | 1.143% | 0 | 0 | 1.2e-05 | 1e-05
49 | 44 | 17 | 38 | 0 | 0 | heating mode | 19% | 1 | 3 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 18% | 2 | 0 | 54% | 75 | 70 | 1.086% | 0 | 0 | 2e-06 | 2e-06
48 | 43 | 212 | 84 | 0 | 0 | heating mode | 18% | 14 | 6 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 20% | 23 | 0 | 51% | 75 | 70 | 1.029% | 0 | 0 | 2.3e-05 | 2e-05
47 | 42 | 12 | 1 | 1 | 0 | heating mode | 16% | 1 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 22% | 1 | 0 | 49% | 75 | 70 | 0.971% | 0 | 0 | 1e-06 | 1e-06
46 | 41 | 215 | 97 | 1 | 0 | heating mode | 14% | 12 | 5 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 23% | 28 | 0 | 46% | 75 | 70 | 0.914% | 0 | 0 | 2.4e-05 | 2.1e-05
45 | 41 | 3 | 3 | 0 | 0 | heating mode | 12% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 25% | 0 | 0 | 43% | 75 | 71 | 0.857% | 0 | 0 | 0 | 0
44 | 39 | 246 | 116 | 0 | 0 | heating mode | 11% | 10 | 5 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 27% | 36 | 0 | 40% | 75 | 71 | 0.8% | 0 | 0 | 2.7e-05 | 2.4e-05
43 | 38 | 5 | 2 | 0 | 0 | heating mode | 9% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 28% | 1 | 0 | 37% | 75 | 71 | 0.743% | 0 | 0 | 1e-06 | 0
42 | 37 | 251 | 116 | 0 | 0 | heating mode | 7% | 7 | 3 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 30% | 42 | 0 | 34% | 75 | 72 | 0.686% | 0 | 0 | 2.7e-05 | 2.4e-05
41 | 36 | 138 | 1 | 1 | 0 | heating mode | 5% | 3 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 32% | 24 | 0 | 31% | 75 | 72 | 0.629% | 0 | 0 | 1.4e-05 | 1.3e-05
40 | 35 | 8 | 56 | 0 | 0 | heating mode | 4% | 0 | 1 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 33% | 1 | 0 | 29% | 75 | 72 | 0.571% | 0 | 0 | 1e-06 | 1e-06
39 | 35 | 245 | 97 | 3 | 0 | heating mode | 2% | 2 | 1 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 35% | 47 | 0 | 26% | 75 | 72 | 0.514% | 0 | 0 | 2.3e-05 | 2e-05
38 | 34 | 16 | 6 | 1 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 37% | 3 | 0 | 23% | 75 | 73 | 0.457% | 0 | 0 | 1e-06 | 1e-06
37 | 33 | 278 | 138 | 5 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 38% | 59 | 0 | 20% | 75 | 73 | 0.4% | 0 | 0 | 2.2e-05 | 2e-05
36 | 32 | 34 | 17 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 40% | 8 | 0 | 17% | 75 | 73 | 0.343% | 0 | 0 | 2e-06 | 2e-06
35 | 31 | 284 | 115 | 7 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 42% | 65 | 0 | 14% | 75 | 74 | 0.286% | 0 | 0 | 1.8e-05 | 1.6e-05
34 | 30 | 30 | 20 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 43% | 7 | 0 | 11% | 75 | 74 | 0.229% | 0 | 0 | 2e-06 | 1e-06
33 | 29 | 275 | 122 | 3 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 45% | 68 | 0 | 9% | 75 | 74 | 0.171% | 0 | 0 | 1.1e-05 | 1e-05
32 | 28 | 168 | 18 | 6 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 47% | 43 | 0 | 6% | 75 | 74 | 0.114% | 0 | 0 | 5e-06 | 4e-06
31 | 27 | 45 | 74 | 3 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 48% | 12 | 0 | 3% | 75 | 75 | 0.057% | 0 | 0 | 1e-06 | 1e-06
30 | 26 | 269 | 84 | 10 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 50% | 74 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
29 | 25 | 36 | 12 | 2 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 52% | 10 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
28 | 24 | 223 | 69 | 6 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 53% | 66 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
27 | 23 | 37 | 11 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 55% | 11 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
26 | 22 | 226 | 84 | 6 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 57% | 71 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
25 | 21 | 42 | 20 | 3 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 58% | 14 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
24 | 20 | 204 | 77 | 10 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 60% | 68 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
23 | 19 | 112 | 22 | 6 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 62% | 38 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
22 | 18 | 37 | 43 | 3 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 63% | 13 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
21 | 17 | 155 | 57 | 4 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 65% | 56 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
20 | 16 | 19 | 9 | 1 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 67% | 7 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
19 | 16 | 95 | 54 | 4 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 68% | 36 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
18 | 15 | 19 | 12 | 2 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 70% | 7 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
17 | 14 | 94 | 57 | 8 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 72% | 37 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
16 | 13 | 20 | 10 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 73% | 8 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
15 | 12 | 102 | 45 | 5 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 75% | 42 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
14 | 11 | 50 | 8 | 1 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 77% | 21 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
13 | 10 | 35 | 33 | 1 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 78% | 15 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
12 | 9 | 83 | 37 | 3 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 80% | 37 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
11 | 8 | 22 | 7 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 82% | 10 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
10 | 7 | 73 | 40 | 5 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 83% | 34 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
9 | 6 | 15 | 8 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 85% | 7 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
8 | 5 | 41 | 22 | 3 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 87% | 20 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
7 | 4 | 10 | 6 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 88% | 5 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
6 | 4 | 40 | 17 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 90% | 20 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
5 | 3 | 20 | 4 | 1 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 92% | 10 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
4 | 2 | 6 | 7 | 1 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 93% | 3 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
3 | 0 | 23 | 8 | 2 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 95% | 12 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
2 | 0 | 11 | 3 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 97% | 6 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
1 | -1 | 13 | 7 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 98% | 7 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
0 | -2 | 2 | 1 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 100% | 1 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
-1 | -3 | 7 | 4 | 1 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 100% | 4 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
-2 | -4 | 2 | 0 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 100% | 1 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
-3 | -5 | 5 | 2 | 1 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 100% | 3 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
-4 | -6 | 2 | 1 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 100% | 1 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
-5 | -6 | 0 | 1 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
-6 | -6 | 2 | 2 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 100% | 1 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
-7 | -6 | 0 | 0 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
-8 | -6 | 2 | 1 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 100% | 1 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
-9 | -6 | 2 | 1 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 100% | 1 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
-10 | -6 | 3 | 0 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 100% | 2 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
-11 | -6 | 2 | 0 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 100% | 1 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
-12 | -6 | 1 | 0 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 100% | 1 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
-13 | -6 | 0 | 0 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
-14 | -6 | 0 | 0 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
-15 | -6 | 0 | 0 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
-16 | -6 | 0 | 0 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
-17 | -6 | 0 | 0 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
-18 | -6 | 0 | 0 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
-19 | -6 | 0 | 0 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
-20 | -6 | 0 | 0 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
-21 | -6 | 0 | 0 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
-22 | -6 | 0 | 0 | 0 | 0 | heating mode | 0% | 0 | 0 | 0 | 100% | 55 | 60 | 5% | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0% | 75 | 75 | 0% | 0 | 0 | 0 | 0
Total |  | 8760 | 3984 | 124 | 368 | [12 empty] | 0.17893 | 0.11609 | [9 empty] | 0.000296 | 0.000263

## DCV (hidden)
Savings Type | Theoretical Savings | Discussion
Cooling: | Yes | DCV can generate cooling savings. The problem is cooling is about 1 kWh/ft2 (2012 CBECs data, modified to account for less heat load from lighting, drives on pumps and fans). If the OAT is 72 or less the Economizer will prevail over DCV, reducing the amount of cooling season eligible.
Heating: | Yes | DCV is often oversold and frequently disconnected by facilities. For the right application it can be a solid measure such as for an auditorium. DCV can compete with economizing if not implemented appropriately. When the air conditioning savings from the economizer surpass the potential savings from reduced airflow, the economizer should override the DCV system.
Assumption 1 - Assumes that of the occupied time period, 20% will be low occupancy- the CO2 levels will be below the ppm thresholds and keep the OA damper at minimum.
Assumption 2 -This worksheet assumed DCV would be overridden by economizer 40% of the time. In other words, the OA damper would remain closed 60% of the time in cooling during occupied when the Demand Control conditions are appropriate, thereby reducing DCV specific savings from 100% to 60%.
Assumption 3 - The estimated reduction of mechanical cooling for times when DCV occurs preventing greater flow of air for cooling through the system
Assumption 4 -This worksheet assumed DCV could be implemented 20% of the occupied time. This 20% is representative of times when DCV can maintain the minimum outside air because the temperature or enthalpy conditions are not eligible to open the OA damper for economizing, but the OA damper would open because the concentration of CO2 is in the space is high enough to open the outside air damper.
Pumps/Fans: | No | Most DCV sequence of operation do not change the supply CFM, only vary the amount of OA and RA. Even in cases where tehre are fan savings, they are not significant compared to cooling and heating savings.
Formula
Cooling Savings | = | Cooling EUI * % Time in low Occ * % Eligible * % Reduction in Cooling
Heating Savings | = | Potential DCV Savings * % Qualifies for DCV
Potential DCV Savings | = | Design Flow * 1.08 * (Balance Point - Mixed Air Temp) * Occupied Hours / (1000 * Boiler Eff)
Where
Cooling | Cooling EUI | 0.8175 | kWh/sqft
Assumption 1 | % Time Low Occupancy | 20%
Assumption 2 | % of eligible cooling not locked out by economizer | 60%
Assumption 3 | % Reduction in Cooling | 50%
Heating | constant | 1.08
| conversion | 1000
| Return Air Temperature | 70 | deg F
| Non-Condensing Boiler Eff | 0.82
| Condensing Boiler Eff | 0.92
| CV - Design Flow | 0.9 | CFM/ft2
| VAV - Design flow | 0.63 | CFM/ft2
| % OA - CV | 15%
% OA in heating mode- VAV
| Balance point - CV, Occupied | 66 | deg F
| Balance point - VAV, Occupied | 62 | deg F
Assumption 4 | % occupied time site qualifies for DCV | 20%
Savings |  |  |  | ** Savings is based on a lesser overall ventilation rate in occ and unocc.
Cooling | 0.04905 | kWh/ft2 |  | using modulating OA damper and CO2 sensor. Usually requires a TAB contractor
Heating - Non-Cond | 0.80326 | kbtu/ft2
Heating - Cond | 0.71595 | kbtu/ft2 | Note - theoretical savings were developed for Condensing Boilers, but ultimately is not used directly in the Savings Factors tables.
| TMY 3 data Worcester |  |  | Occupancy |  | Mixed Air Temp |  | Potential DCV Savings
Mode | Bin | average temp | hrs/yr | Occupied Hours (M-F 6AM to 6PM hrs/yr) | Unocc hrs | CV | VAV | CV - Non-cond Boiler | VAV - Non-cond Boiler | Condensing Boiler
Cooling | 95 to 99 | 97 | 0 | 0 | 0 | 66 | 62
Cooling | 90 to 94 | 92 | 0 | 0 | 0 | 66 | 62
Cooling | 85 to 89 | 87 | 25 | 20 | 5 | 66 | 62
Cooling | 80 to 84 | 82 | 125 | 91 | 34 | 66 | 62
Cooling | 75 to 79 | 77 | 336 | 236 | 100 | 66 | 62
Cooling | 70 to 74 | 72 | 423 | 239 | 184 | 66 | 62
Cooling | 65 to 69 | 67 | 718 | 309 | 409 | 66 | 62
Cooling | 60 to 64 | 62 | 1050 | 328 | 722 | 66 | 62
Cooling | 55 to 59 | 57 | 793 | 259 | 534 | 66 | 62 | 0 | 0 | 0
Heating | 50 to 54 | 52 | 646 | 236 | 410 | 66 | 62 | 0 | 0 | 0
Heating | 45 to 49 | 47 | 459 | 182 | 277 | 66 | 62 | 0 | 0 | 0
Heating | 40 to 44 | 42 | 648 | 212 | 436 | 65.8 | 62 | 0.05026 | 0 | 0.044797
Heating | 35 to 39 | 37 | 857 | 275 | 582 | 65.05 | 62 | 0.30968 | 0 | 0.27602
Heating | 30 to 34 | 32 | 787 | 287 | 500 | 64.3 | 62 | 0.57834 | 0 | 0.51548
Heating | 25 to 29 | 27 | 564 | 198 | 366 | 63.55 | 62 | 0.57502 | 0 | 0.51252
Heating | 20 to 24 | 22 | 527 | 176 | 351 | 62.8 | 62 | 0.6676 | 0 | 0.59503
Heating | 15 to 19 | 17 | 330 | 152 | 178 | 62.05 | 62 | 0.71169 | 0 | 0.63434
Heating | 10 to 14 | 12 | 263 | 88 | 175 | 61.3 | 62 | 0.49027 | 0 | 0.43698
Heating | 5 to 9 | 7 | 126 | 59 | 67 | 60.55 | 62 | 0.38115 | 0 | 0.33972
Heating | 0 to 4 | 2 | 55 | 25 | 30 | 59.8 | 62 | 0.18373 | 0 | 0.16376
Heating | -1 to -5 | -3 | 16 | 5 | 11 | 59.05 | 62 | 0.041191 | 0 | 0.036714
Heating | -6 to -10 | -8 | 9 | 3 | 6 | 58.3 | 62 | 0.027382 | 0 | 0.024406
Heating | -11 to -15 | -13 | 3 | 0 | 3 | 57.55 | 62 | 0 | 0 | 0
| totals |  | 8760 | 3380 | 5380 |  |  | 4.0163 | 0 | 3.5798

## CHW Reset (hidden)
Savings Type | Theoretical Savings | Discussion
Cooling: | Yes | Chilled Water Reset has some savings potential if the internal loads do not dominate the need for cooling. Although BMS cooling strategies are perfectly legitimate recommendations for many applications, in New England it is a minor contributor. This value is probably high. A significant heat source is from plug load, lighting, people and solar gain. To say the cooling load is reduced just on OAT ignores the impact from internal heat sources. Secondly the ability to reset the CH temp will range from highly probable, during moderately load, to unlikely when cooling is at a high load. To assume its enabled at 5 F for roughly 40% of the cooling season is too simplistic and overstates the savings.
Heating: | No
Pumps/Fans: | No
Formula
Cooling Savings | = | Cooling EUI * (Avg Temp Increase * Reduced Compressor Power/deg) * %Cooling energy for compressor *hours CHW reset / Total cooling hours
Where
Cooling EUI | 0.8175 | kWh/ft2
Ave Temp Increase in Chilled Water | 5 | deg F
Reduced Compressor power/deg | 2%
% Cooling energy from compressor | 85%
Cooling hours for CHW reset | 1482 | hours
Total Cooling Hours | 3470 | hours
Savings
Cooling Savings | 0.029677

## HW Reset (hidden)
Savings Type | Theoretical Savings | Discussion
Cooling: | No
Heating: | Yes | This strategy reduces the temperature of the distrubution hydronic heating lines. The basecase assumption is that the distribution piping is insulated. Savings are reduced losses from the insulation due to the lower temperature. Insulated pipe still loses energy although at a reduced rate. The lower the solution's (water in this case) temperature the less heat lost from the insulation. Insulation loss is easily determined from energy calculators such as the National Mechanical Insulation Committee's calculator for horizontal piping. The base case distribution loss is estimated to be 8%. This suggests the energy delivered to the heat emitters (coils at RTUs, FCUs, terminal boxes, radiators etc.) is about 72% of the HHV. If the boiler's combustion and radiant loss is 20%, destribution piping loss is 8% then 72 % is delivered to heat emitters.
Pumps/Fans: | No
Formula
Non-Condensing Boiler Savings | = | Condensing Boiler Heating EUI * (%reduction losses per linear foot) * distribution losses
Condensing Boiler Savings | = | Non-Condensing EUI * (%reduction losses per linear foot) * distribution losses
Where
| Heating System Distribution Loss % | 10% |  | Engineering Estimate
| Heating EUI | 32.4744 | Mbtu/ft2
Non-Condensing Boiler | Baseline - Loss per linear foot - 4" pipe | 31 | Btu/hr/ft | National Mechanical Insulation Committee's Energy Calculator for Horizontal Piping (180 deg F average hydronic line temp)
| Proposed - Loss per linear foot - 4" pipe | 24 | Btu/hr/ft | National Mechanical Insulation Committee's Energy Calculator for Horizontal Piping (160 deg F average hydronic line temp with OA reset)
Condensing Boiler | Non-Condensing Boiler Eff | 0.82
| Baseline - Loss per linear foot - 4" pipe | 24 | Btu/hr/ft | National Mechanical Insulation Committee's Energy Calculator for Horizontal Piping (160 deg F average hydronic line temp)
| Proposed - Loss per linear foot - 4" pipe | 19 | Btu/hr/ft | National Mechanical Insulation Committee's Energy Calculator for Horizontal Piping (145 deg F average hydronic line temp with OA reset)
| Condensing Boiler Eff | 0.92
Savings
Non-Condensing % Reduction in losses | 22.58%
Non-Condensing Boiler Savings | 0.73329 | Mbtu/ft2
Condensing % Reduction in losses | 20.83%
Condensing Boiler Savings | 0.67655 | Mbtu/ft2 | Note - theoretical savings were developed for Condensing Boilers, but ultimately is not used directly in the Savings Factors tables.

## Economizer (hidden)
Savings Type | Theoretical Savings | Discussion
Cooling: | Yes | Economizing can generate cooling savings. The problem is cooling is about 1 kWh/ft2 (2012 CBECs data, modified to account for less heat load from lighting, drives on pumps and fans). Economizer will prevail over DCV, increasing the amount of cooling season eligible.
Economizing is often overridden or overcomplicated in facilities if the comparison of return or OA temps or enthalpy readings are inaccurate or programmed incorrectly.
Assumption 1 - The amount of time comparison between OAT and RAT dry bulb temps or enthalpy allow for Economizing to occur. Based on the psychometric chart covered by IECC Region 5A in https://www.researchgate.net/figure/Psychrometric-chart-regions-based-on-the-recommended-envelope-11_fig6_313626195
Assumption 2 -Economizing is only likely to occur when the outside air temperature is greater than freezing and less than 72 degF. For cooling temps, this is limited to 2,984 hrs of the TMY3 data, which is 86% of the year.
Assumption 3 - Percentage of mechanical cooling reduced when outdoor air is used for free cooling. Same assumption used in DCV.
Heating: | No
Pumps/Fans: | No | Most Econ sequences of operation do not change the supply CFM, only vary the amount of OA and RA.
Formulas
Cooling Savings | = | Cooling EUI * % Time Econ Conditions Optimal * % Eligible * % Mechancial Cooling Reduction
Where
Cooling | Cooling EUI | 0.8175 | kWh/sqft
| % of time economizing conditions optimal | 46%
| % of eligible TMY3 cooling band by economizer | 86%
| % Reduction in Mechanical Cooling | 50%
Savings
Cooling | 0.1617 | kWh/ft2
| TMY 3 data Worcester |  |  | Occupancy |  | Mixed Air Temp |  | Estimated Design Conditions
Mode | Bin | average temp | hrs/yr | Occupied Hours (M-F 6AM to 6PM hrs/yr) | Unocc hrs | CV | VAV | RAT | 70 | degF
Cooling | 95 to 99 | 97 | 0 | 0 | 0 | 66 | 62 | DAT_SP | 55 | degF
Cooling | 90 to 94 | 92 | 0 | 0 | 0 | 66 | 62
Cooling | 85 to 89 | 87 | 25 | 20 | 5 | 66 | 62
Cooling | 80 to 84 | 82 | 125 | 91 | 34 | 66 | 62
Cooling | 75 to 79 | 77 | 336 | 236 | 100 | 66 | 62
Cooling | 70 to 74 | 72 | 423 | 239 | 184 | 66 | 62
Cooling | 65 to 69 | 67 | 718 | 309 | 409 | 66 | 62
Cooling | 60 to 64 | 62 | 1050 | 328 | 722 | 66 | 62
Cooling | 55 to 59 | 57 | 793 | 259 | 534 | 66 | 62
Heating | 50 to 54 | 52 | 646 | 236 | 410 | 66 | 62
Heating | 45 to 49 | 47 | 459 | 182 | 277 | 66 | 62 |  | 0.46657 | Supply 55degF by blending Supply air with Return air
Heating | 40 to 44 | 42 | 648 | 212 | 436 | 65.8 | 61.6 |  |  | At higher OAT, may have a penalty bc some humidity
Heating | 35 to 39 | 37 | 857 | 275 | 582 | 65.05 | 60.1
Heating | 30 to 34 | 32 | 787 | 287 | 500 | 64.3 | 58.6
Heating | 25 to 29 | 27 | 564 | 198 | 366 | 63.55 | 57.1
Heating | 20 to 24 | 22 | 527 | 176 | 351 | 62.8 | 55.6
Heating | 15 to 19 | 17 | 330 | 152 | 178 | 62.05 | 54.1
Heating | 10 to 14 | 12 | 263 | 88 | 175 | 61.3 | 52.6
Heating | 5 to 9 | 7 | 126 | 59 | 67 | 60.55 | 51.1
Heating | 0 to 4 | 2 | 55 | 25 | 30 | 59.8 | 49.6
Heating | -1 to -5 | -3 | 16 | 5 | 11 | 59.05 | 48.1
Heating | -6 to -10 | -8 | 9 | 3 | 6 | 58.3 | 46.6
Heating | -11 to -15 | -13 | 3 | 0 | 3 | 57.55 | 45.1
| totals |  | 8760 | 3380 | 5380